| Bid Solicitation # | 25DPP01146 |
| --- | --- |
| T2946 – Elevator Maintenance, Repair, Testing, and Inspection Services - Statewide |  |

|  | Date | Time |
| --- | --- | --- |
| Due Date For Electronic Questions Refer to Bid Solicitation Section 2.1 for more information. | 5/04/26 | 2:00 PM |
| Optional Pre-Quote Submission Conference Refer to Bid Solicitation Section 2.5 for more information. | 4/27/26 | 10:30 AM |
| Mandatory/Optional Site Visit Refer to Bid Solicitation Section 2.4 for more information. | N/A | N/A |
| Quote Opening Date Refer to Bid Solicitation Section 3 for more information. | 6/23/26 | 2:00 PM |

Dates are subject to change.  All times contained in the Bid Solicitation refer to Eastern Time.

All changes will be reflected in Bid Amendments to the Bid Solicitation posted on www.njstart.gov.

| SET-ASIDES |  |
| --- | --- |
| Small Business Set-Aside For Goods and Services: ☒ I ☒ II ☒ III For Construction: ☐ IV ☐ V ☐ VI | ☐ Not Applicable ☐ Entire Contract ☒ Partial Contract ☐ Subcontracting Only ☐ Preference |
| Disabled Veteran-Owned Business Set-Aside | ☒ Not Applicable ☐ Entire Contract ☐ Partial Contract ☐ Subcontracting Only ☐ Preference |

| Bid Solicitation Issued By: State of New Jersey Department of the Treasury Division of Purchase and Property Trenton, New Jersey 08625-0230 | On Behalf of: State of New Jersey Cooperative Purchasing Participants |
| --- | --- |

Date:  6/4/2026

TABLE OF CONTENTS

1	INTRODUCTION AND SUMMARY OF THE BID SOLICITATION	1

1.1	PURPOSE, AND INTENT AND BACKGROUND	1

1.2	BACKGROUND	2

1.2.1	REGIONS	2

1.3	CONTRACT AMOUNT	2

1.4	ORDER OF PRECEDENCE OF CONTRACTUAL TERMS	3

1.5	INTRASTATE COOPERATIVE PURCHASING	3

2	PRE-QUOTE SUBMISSION INFORMATION	4

2.1	ELECTRONIC QUESTION AND ANSWER PERIOD	4

2.2	EXCEPTIONS TO THE STATE OF NJ STANDARD TERMS AND CONDITIONS (SSTC)	4

2.3	BID AMENDMENTS	4

2.4	MANDATORY/OPTIONAL SITE VISIT	4

2.5	OPTIONAL PRE-QUOTE CONFERENCE	4

2.6	PRE-QUOTE DOCUMENT REVIEW	4

3	QUOTE SUBMISSION REQUIREMENTS	5

3.1	QUOTE SUBMISSION	5

3.2	BIDDER RESPONSIBILITY	5

3.3	ANNOUNCEMENT OF QUOTE INFORMATION	5

3.4	QUOTE ERRORS	5

3.5	QUOTE WITHDRAWAL PRIOR TO QUOTE OPENING	5

3.6	QUOTE WITHDRAWAL AFTER QUOTE OPENING, BUT PRIOR TO CONTRACT AWARD	5

3.7	JOINT VENTURE	6

3.8	SMALL BUSINESS SET-ASIDE CONTRACTS	6

3.9	DISABLED VETERANS’ BUSINESS SET-ASIDE CONTRACT	6

3.10	BID SECURITY	6

3.11	BIDDER ADDITIONAL TERMS SUBMITTED WITH THE QUOTE	6

3.12	QUOTE CONTENT	7

3.13	FORMS, REGISTRATIONS AND CERTIFICATIONS TO BE SUBMITTED WITH QUOTE	7

3.13.1	OFFER AND ACCEPTANCE PAGE	7

3.13.2	OWNERSHIP DISCLOSURE FORM	7

3.13.3	DISCLOSURE OF INVESTMENT ACTIVITIES IN IRAN FORM	7

3.13.4	DISCLOSURE OF INVESTIGATIONS AND OTHER ACTIONS INVOLVING BIDDER FORM	8

3.13.5	MACBRIDE PRINCIPLES FORM	8

3.13.6	SERVICE PERFORMANCE WITHIN THE UNITED STATES	8

3.13.7	CONFIDENTIALITY/COMMITMENT TO DEFEND	8

3.13.8	SUBCONTRACTOR UTILIZATION PLAN	9

3.13.9	RESERVED	9

3.13.10	AFFIRMATIVE ACTION	9

3.13.11	RESERVED	9

3.13.12	STATE OF NEW JERSEY SECURITY DUE DILIGENCE THIRD-PARTY INFORMATION SECURITY QUESTIONNAIRE	9

3.13.13	BUSINESS REGISTRATION	9

3.13.14	Certification of Non-Involvement in Prohibited Activities in Russia or Belarus Pursuant to P.L.2022, c.3	10

3.14	BIDDER QUOTE OVERVIEW FORM	10

3.15	BIDDER DATA SHEET/FORM	10

3.16	EXPERIENCE WITH CONTRACTS OF SIMILAR SIZE AND SCOPE	10

3.17	PUBLIC WORKS CONTRACTOR REGISTRATION	11

3.18	FINANCIAL CAPABILITY OF THE BIDDER	11

3.19	STATE-SUPPLIED PRICE SHEET INSTRUCTIONS	11

3.19.1	BID-SPECIFIC STATE-SUPPLIED PRICE SHEET INSTRUCTIONS	12

3.19.2	USE OF “NO BID” VERSUS “NO CHARGE” ON THE STATE-SUPPLIED PRICE SHEET	13

4	SCOPE OF WORK	14

4.1	CONTRACTOR REQUIREMENTS	14

4.2	SERVICE HOURS	14

4.2.1	HOURLY LABOR REPAIR RATES	15

4.2.2	OVERTIME PAY RATE	15

4.2.3	PREMIUM PAY RATE	15

4.2.4	SIGN-IN/SIGN-OUT PROCEDURE	15

4.3	CALLBACK SERVICE	15

4.4	MAINTENANCE RESPONSIBILITIES	16

4.5	ADDITIONAL SERVICES	17

4.6	MAINTENANCE SCHEDULE	18

4.6.1	GEARLESS, GEARED, AND HYDRAULIC ELEVATORS	18

4.6.2	ESCALATORS	20

4.7	NJDOT MOVEABLE BRIDGE ELEVATOR REQUIREMENTS	21

4.8	SAFETY INSPECTION AND TESTS	22

4.9	PARTS AND MATERIALS	22

4.9.1	PURCHASE OF PARTS AND MATERIALS	22

4.10	CONTRACTOR FURNISHED MATERIALS AND TOOLS	23

4.11	RECORDS	23

4.12	REIMBURSABLE SERVICES	23

4.13	CONTRACTOR PERSONNEL	24

4.14	SAFE WORK PRACTICES	24

4.15	ACCIDENT AND SAFETY REPORTS AND INVESTIGATIONS	25

4.16	SECURITY CLEARANCES	25

4.16.1	STATE HOUSE COMPLEX-SPECIFIC BACKGROUND CHECKS & REIMBURSEMENT	25

4.16.2	CRIMINAL HISTORY RECORD	26

4.16.3	CRIMINAL HISTORY RECORD FILE	26

4.17	NJDOC – ADDITIONAL SECURITY REQUIREMENTS	26

4.18	PUBLIC WORKS CONTRACTOR REGISTRATION	26

4.19	PREVAILING WAGE	26

4.20	CERTIFIED PAYROLL RECORDS	27

4.21	METHOD OF OPERATION	27

4.22	GEOGRAPHICAL REGIONS	27

5	GENERAL CONTRACT TERMS	28

5.1	CONTRACT TERM AND EXTENSION OPTION	28

5.2	CONTRACT TRANSITION	28

5.3	PERFORMANCE SECURITY	28

5.4	OWNERSHIP OF MATERIAL	28

5.5	SUBSTITUTION OF STAFF	29

5.6	DELIVERY TIME AND COSTS	29

5.7	AUTHORIZED DEALER AND/OR DISTRIBUTORS	29

5.8	LIQUIDATED DAMAGES	29

5.9	RETAINAGE	29

5.10	ELECTRONIC PAYMENTS	30

5.11	PROCUREMENT EFFICIENCY PROGRAM	30

6	DATA SECURITY REQUIREMENTS – CONTRACTOR RESPONSIBILITY	31

7	MODIFICATIONS TO THE STATE OF NEW JERSEY STANDARD TERMS AND CONDITIONS	32

7.1	INSURANCE	32

7.1.1	PROFESSIONAL LIABILITY INSURANCE	32

8	QUOTE EVALUATION AND AWARD	33

8.1	RIGHT TO WAIVE	33

8.2	DIRECTOR’S RIGHT TO ACCEPT OR REJECT A QUOTE	33

8.3	RECIPROCITY FOR JURISDICTIONAL BIDDER PREFERENCE	33

8.4	CLARIFICATION OF QUOTE	33

8.5	ORAL PRESENTATION	33

8.6	TIE QUOTES	33

8.7	STATE'S RIGHT TO INSPECT BIDDER’S FACILITIES	33

8.8	STATE'S RIGHT TO CHECK REFERENCES	33

8.9	EVALUATION CRITERIA	34

8.9.1	TECHNICAL EVALUATION CRITERIA	34

8.9.2	PRICE EVALUATION	34

8.10	QUOTE DISCREPANCIES	34

8.11	NEGOTIATION	34

8.12	BEST AND FINAL OFFER (BAFO)	34

8.13	“REQUEST FOR REVISION” WITHIN NJSTART	35

8.14	POOR PERFORMANCE	35

8.15	RECOMMENDATION FOR AWARD	35

8.16	CONTRACT AWARD	35

9	GLOSSARY	36

9.1	CROSSWALK	36

9.2	DEFINITIONS	36

9.3	CONTRACT-SPECIFIC DEFINITIONS	42

ATTACHMENT 1 – Combined State of New Jersey Standard Terms and Conditions (6/3/2025)

ATTACHMENT 2 – Standard Procurement Forms Packet

ATTACHMENT 3 – Bidder Data Form

ATTACHMENT 4 – Quote Overview Form

ATTACHMENT 5 – Pre-Quote Conference PowerPoint Presentation

ATTACHMENT 6 – State Location List

ATTACHMENT 7 – New Jersey State House Complex Procedure for Background Checks

# INTRODUCTION AND SUMMARY OF THE BID SOLICITATION

This Bid Solicitation is issued by the Department of the Treasury, Division of Purchase and Property (Division), Procurement Bureau, on behalf of the State of New Jersey. Quotes submitted in response to this Bid Solicitation shall be through the State of New Jersey’s eProcurement system, NJSTART.  Bidders are advised to thoroughly read all sections of this Bid Solicitation and follow all instructions.

Bidders are strongly encouraged to visit the NJSTART Vendor Support Page, which contains Quick Reference Guides (QRGs), supporting videos, a glossary of NJSTART terms, and helpdesk contact information.  Bidders should utilize the QRGs before attempting to submit a Quote through NJSTART.   It is the Bidder’s responsibility to ensure that the Quote and attachments have been properly submitted.  Inquiries concerning the use of NJSTART may be directed to njstart@treas.nj.gov. The Division will not respond to substantive questions related to the Bid Solicitation or any other Contract via this email address.

## PURPOSE, AND INTENT AND BACKGROUND

The purpose of this Bid Solicitation is to solicit Quotes for maintenance, repair, testing, and inspection services for vertical transportation equipment in State owned buildings, the New Jersey Department of Transportation’s moveable bridge elevators and for all Using Agencies and intrastate Cooperative Purchasing Program participants within the State.

It is the intent of the State to award Contracts to those responsible Bidders whose Quotes, conforming to this Bid Solicitation are most advantageous to the State of New Jersey (State), price and other factors considered.  The State may award any or all price lines.  The State, however, reserves the right to separately procure individual requirements that are the subject of the Contract during the Contract term, when deemed by the Director of the Division (Director) to be in the State’s best interest.

There are fifty-two (52) price lines, which are grouped and itemized as follows:

| Group Number | Price Line Numbers |
| --- | --- |
| Group 1 – North Region | 1 – 13 |
| Group 2 – Central Region | 14 – 26 |
| Group 3 – South Region | 27 – 39 |
| Group 4 – Capitol Complex | 40 – 52 |

Each of the four (4) regions contains the same thirteen (13) price lines, divided as follows:

| Price Line | Service | Unit of Measure |
| --- | --- | --- |
| 1 | Mechanic - Regular Rate | Hour |
| 2 | Mechanic - Overtime Rate | Hour |
| 3 | Mechanic - Premium Rate | Hour |
| 4 | Helper - Regular Rate | Hour |
| 5 | Helper - Overtime Rate | Hour |
| 6 | Helper - Premium Rate | Hour |
| 7 | Adjuster - Regular Rate | Hour |
| 8 | Adjuster - Overtime Rate | Hour |
| 9 | Adjuster - Premium Rate | Hour |
| 10 | Team - Regular Rate | Hour |
| 11 | Team - Overtime Rate | Hour |
| 12 | Team - Premium Rate | Hour |
| 13 | % markup for materials/supplies (not to exceed 10%) | Percentage |

Bidders are able to Bid on one (1) group, all groups, or any combination thereof. Bidders must bid on the first twelve (12) price lines contained within a group (example: Group 1 Price Lines 1 – 12) in order to be considered responsive for that group. A Bidder may bid on the thirteenth (13th) price line in a group. If a Bidder does not bid on the first twelve (12) price lines within a group, its Quote will be considered non-responsive for that group only. Each Group will be evaluated and awarded separately. Quotes will be evaluated in accordance with Bid Solicitation Section 8.0, Quote Evaluation and Award. The State intends to award one (1) or more Contracts per group (Group 1 – North Region, Group 2 – Central Region, Group 3 – South Region, and Group 4 – Capitol Complex), in accordance with Section 8.16, Contract Award of this Bid Solicitation. Each region may have up to six (6) Contracts. Using Agencies will be able to utilize the awarded Contractors per group following the methodology demonstrated in Bid Solicitation Section 4.21, Method of Operation.

This Bid Solicitation has been designated as a partial Small Business set-aside Contract for Small Business Category I, II or III, as per Bid Solicitation Section 3.8, Small Business Set-Aside Contracts. The State intends to award to at least one (1) qualifying small business in each Region.

If no responsive Quotes with acceptable pricing are received from qualified Small Businesses, the Division will award those set-aside Contracts to non-Small Business Bidders.

The State of New Jersey Standard Terms and Conditions (SSTCs) included with this Bid Solicitation will apply to all Contracts made with the State.  These terms are in addition to the terms and conditions set forth in this Bid Solicitation and should be read in conjunction with them unless the Bid Solicitation specifically indicates otherwise.

## BACKGROUND

This is a reprocurement of the services under T2946 - Elevator Maintenance, Repair, Testing, and Inspection Services.  Bidders interested in reviewing the expiring Contract’s specifications and pricing information may do so by following the instructions below.  Bidders should not rely upon or use data or information from the expiring Contract when preparing a response to this Bid Solicitation as this Bid Solicitation addresses the State’s current requirements.

- Go to: www.njstart.gov

- In the search bar, select “Contracts” from the drop down menu

- Enter “T2946” and click “”

- The expiring Contract list will appear under “Results”

### REGIONS

For the purposes of this Bid Solicitation, the State has been divided into four (4) separate regions as follows: North, Central, South, and Capitol Complex. Counties comprising each of the first three regions are indicated below:

| Region 1 - North | Region 2 - Central | Region 3 - South | Region 4 – Capitol Complex |
| --- | --- | --- | --- |
| Bergen County | Hunterdon County | Atlantic County | See Attachment #6 – State Location List |
| Essex County | Mercer County | Burlington County |  |
| Hudson County | Middlesex County | Camden County |  |
| Morris County | Monmouth County | Cape May County |  |
| Passaic County | Somerset County | Cumberland County |  |
| Sussex County |  | Gloucester County |  |
| Union County |  | Ocean County |  |
| Warren County |  | Salem County |  |

The Capitol Complex (Region 4) is designated as a separate region separate from the Central Region, and contains specific buildings within Trenton as outlined by Attachment #6 – State Location List.

## CONTRACT AMOUNT

The estimated amount of the Contract, if stated, shall not be construed as either the maximum or minimum amount which the State shall be obliged to order.

## ORDER OF PRECEDENCE OF CONTRACTUAL TERMS

The Contract awarded, and the entire agreement between the parties, as a result of this Bid Solicitation shall consist of:  (1) the final Bid Solicitation, (2) the State of New Jersey Standard Terms and Conditions, (3) the Quote, and if applicable (4) any Bidder responses to clarifications; (5) a Bidder’s Best and Final Offer, (6) other negotiated document, and/or (7) third party document.  In the event of a conflict in the terms and conditions among the documents comprising this Contract, the order of precedence, for purposes of interpretation thereof, shall be as listed from highest ranking to lowest ranking as noted above.

Any other terms or conditions, not included with the Bidder’s Quote and accepted by the State, shall not be incorporated into the Contract awarded.  Any references to external documentation, including those documents referenced by a URL, including without limitation, technical reference manuals, technical support policies, copyright notices, additional license terms, etc., are subject to the terms and conditions of the Bid Solicitation and the State of New Jersey Standard Terms and Conditions.  In the event of any conflict between the terms of a document incorporated by reference, the terms and conditions of the Bid Solicitation and the State of New Jersey Standard Terms and Conditions shall prevail.

## INTRASTATE COOPERATIVE PURCHASING

The State intends to extend the Contracts awarded to the State's Intrastate Cooperative Purchasing Participants.  Although the State is making the use of any Contract resulting from this Bid Solicitation available to Intrastate Cooperative Purchasing Participants, the State makes no representation as to the acceptability of the Bid Solicitation’s terms and conditions to any Intrastate Cooperative Purchasing Participants.

# PRE-QUOTE SUBMISSION INFORMATION

The Bidder assumes sole responsibility for the complete effort required in submitting a Quote and for reviewing the Quote submission requirements and the Scope of Work requirements.

## ELECTRONIC QUESTION AND ANSWER PERIOD

The Division will electronically accept questions and inquiries from all potential Bidders via the “Q&A” Tab of the Bid Solicitation in NJSTART.  Questions should be directly tied to a Bid Solicitation Section, the State-Supplied Price Sheet, Form or Attachment; and should reference the specific Bid Solicitation Section or document to which it relates.

The cut-off date for electronic questions and inquiries relating to this Bid Solicitation is indicated on the Bid Solicitation cover page.  In the event that questions are posed by Bidders, answers to such questions will be issued by Bid Amendment.

A Bidder shall not contact the Using Agency and/or the Procurement Specialist directly, in person, by telephone or by e-mail, concerning this Bid Solicitation, prior to Contract award.

## EXCEPTIONS TO THE STATE OF NJ STANDARD TERMS AND CONDITIONS (SSTC)

Questions regarding the State of New Jersey Standard Terms and Conditions and exceptions to mandatory requirements MUST be posed during the Electronic Question and Answer period and shall contain the Bidder’s suggested changes and the reason(s) for the suggested change(s).

## BID AMENDMENTS

In the event that it becomes necessary to clarify or revise this Bid Solicitation, such clarification or revision will be by Bid Amendment.  Any Bid Amendment will become part of this Bid Solicitation and part of any Contract awarded. Bid Amendments will be posted as a file attachment on the “Summary” page of the Bid Solicitation in NJSTART after the cut-off date.

There are no designated dates for release of Bid Amendments.  Those Bidders who are on the bid holder list either through commodity code registration in NJSTART or by acknowledging the bid in NJSTART should receive notification of any Bid Amendment(s). If a Bidder is not on the bid holder list, Bid Amendments are still viewable on the “Summary” page of the Bid Solicitation in NJSTART.

It is the sole responsibility of the Bidder to be knowledgeable of all Bid Amendments related to this procurement. An interested Bidder should check the NJSTART “Open Bids” Tab on a daily basis to ensure review of the most updated information.

## MANDATORY/OPTIONAL SITE VISIT

Not applicable to this procurement.

## OPTIONAL PRE-QUOTE CONFERENCE

The date and time of the Optional Pre-Quote Conference is indicated on the Bid Solicitation cover sheet.  Attendees may attend the Optional Pre-Quote Conference with the following call-in details:

Join the meeting now

Meeting ID: 246 573 902 463 43

Passcode: A3BY3fK3

Or call in (audio only):

Phone Number: 1 856-338-7074

Phone Conference Access Code: 499 774 21#

The Optional Pre-Quote Conference may be recorded.

The purpose of the Optional Pre-Quote Conference is to address procedural questions regarding the Bid Solicitation and Bidder Quote Submission Requirements only.  No substantive questions regarding the Bid Solicitation Scope of Work will be accepted or answered during the pre-Quote conference.  All questions are to be submitted during the Electronic Question and Answer Period.

## PRE-QUOTE DOCUMENT REVIEW

Not applicable to this procurement.

# QUOTE SUBMISSION REQUIREMENTS

## QUOTE SUBMISSION

In order to be considered for award, the Quote must be received electronically by the Division’s Proposal Review Unit, through NJSTART, by the required date and time.

The date and time of the Quote opening are indicated on the Bid Solicitation cover sheet and on the “Summary” Tab of the Bid Solicitation webpage within NJSTART.  If the Quote opening deadline has been revised, the new Quote opening deadline will be shown on the posted Bid Amendment and on the “Summary” Tab of the Bid Solicitation webpage within NJSTART.  Quotes not received prior to the Quote opening deadline shall be rejected.

Quotes will be publicly opened and announced by telephone conference on the date and time of the quote opening.

(Dial-in phone number: 888-204-5984 / Access code: 2602305)

When submitting a Quote through NJSTART, do not use any symbols (i.e., #, @, $, &, *) in the filename as this may prevent the Quote from being properly uploaded.  Uploaded files must be compatible with Microsoft Office and/or Adobe software applications. DO NOT UPLOAD files with extensions such as .zip, .numbers, or .pages.

When uploading the documents to NJSTART, the Bidder should select the “Confidential” option in NJSTART for attachments on the “Attachments” Tab to request that the documents not be displayed publicly through NJSTART. Marking an attachment as "Confidential" in NJSTART shall not constitute the Bidder's designation of the attachment as exempt from public disclosure under the New Jersey Open Public Records Act (OPRA), N.J.S.A. 47:1A-1 et seq., or the common law right to know.

## BIDDER RESPONSIBILITY

The Bidder assumes sole responsibility for the complete effort required in submitting a Quote in response to this Bid Solicitation.  No special consideration will be given after Quotes are opened because of a Bidder’s failure to be knowledgeable as to all of the requirements of this Bid Solicitation.  The State assumes no responsibility and bears no liability for costs incurred by a Bidder in the preparation and submittal of a Quote in response to this Bid Solicitation or any pre-contract award costs incurred.

## ANNOUNCEMENT OF QUOTE INFORMATION

On the date and time Quotes are due under the Bid Solicitation, all information concerning the Quotes submitted may be publicly announced and shall be available for inspection and copying except otherwise noted:

- Information appropriately designated as proprietary and/or confidential in a Bidder’s Quote shall not be available for inspection and copying; and

- Where negotiation is contemplated, only the names and addresses of the Bidders submitting Quotes will be announced, and the contents of the Quotes shall not be available for inspection and copying until the Notice of Intent to Award is issued by the Director.

## QUOTE ERRORS

In accordance with N.J.A.C. 17:12-2.11 “Proposal errors,” a Bidder may withdraw its Quote as described below.

## QUOTE WITHDRAWAL PRIOR TO QUOTE OPENING

A Bidder may withdraw its Quote submission in NJSTART prior to the Quote opening; however, Bidders should note that while withdrawn NJSTART Quotes remain viewable by the Bidder on its Vendor Profile Homepage, they are removed from the Division’s view and cannot be considered for Contract award. The Bidder may submit a revised Quote as long as the Quote is received prior to the announced date and time for Quote submission. Bidders may refer to the QRG “Submit a Quote” for additional instructions.

## QUOTE WITHDRAWAL AFTER QUOTE OPENING, BUT PRIOR TO CONTRACT AWARD

If, after the Quote opening, but before Contract award, a Bidder discovers an error in its Quote, the Bidder may make a written request to the Procurement Bureau to withdraw its Quote, or a portion thereof, from consideration for award.  If the Bidder’s request to withdraw is made in good faith, and the State will not be significantly prejudiced by granting the withdrawal of the Quote beyond the loss of the benefit of the bargain to the State of the withdrawing Bidder’s offer, the request shall be granted.  Evidence of the Bidder’s good faith in making this request can be demonstrated by one (1) or more of the following factors: A mistake is so significant that to enforce the Contract resulting from the Quote would be unconscionable; that the mistake relates to a material feature or term of the Contract; and that the mistake occurred notwithstanding the Bidder’s exercise of reasonable care.  After Quote opening, while pursuant to the provisions of this section a Bidder may request to withdraw its Quote and the Director may in his/her discretion allow said Bidder to withdraw it, the Division also may take notice of repeated or unusual requests to withdraw by a Bidder and take those prior requests to withdraw into consideration when evaluating the Bidder’s future Quotes.

The Quote withdrawal request must include the Bid Solicitation Number, Bid Solicitation Title, and the Quote submission date and should be sent to Procurement.Bureau@treas.nj.gov.

If, during a Quote evaluation process, an obvious pricing error made by a potential Contract awardee is found, the Director or his/her designee shall issue written notice to the Bidder.  The Bidder will have up to five (5) Business Days after receipt of the notice to confirm its pricing.  If the Bidder fails to respond, its Quote shall be considered withdrawn, and no further consideration shall be given to it.

## JOINT VENTURE

If a Joint Venture is submitting a Quote, the agreement between the parties relating to such Joint Venture should be submitted with the Joint Venture’s Quote.  Authorized signatories from each party comprising the Joint Venture must sign the Offer and Acceptance Page.  Each party to the Joint Venture must individually complete and comply with all the forms and certification requirements in Bid Solicitation Section 3 – Quote Submission Requirements.

## SMALL BUSINESS SET-ASIDE CONTRACTS

Pursuant to the provisions of N.J.S.A. 52:32-17 et seq. and N.J.A.C. 17:13 et seq. this is a partial Set-Aside Contract for Category I, II, and III for Small Businesses.  This Bid Solicitation will be evaluated and awarded by region. The State intends to award to at least one (1) registered small business for each region.

If no responsive Quotes with acceptable pricing are received from qualified Small Businesses, the Division will award those set-aside Contracts to non-Small Business Bidders.

The Bidder must be registered as a qualified small business with the Division of Revenue and Enterprise Services, Small Business Registration and M/WBE Certification Services Unit, by the date the Quote is received and opened.

A Bidder should verify its Small, Minority, Veteran, and Women Owned Business Certification status on the “Maintain Terms and Categories” Tab within its profile in NJSTART. In the event of an issue with a Bidder’s Small, Minority, Veteran, and Women Owned Business Certification status, NJSTART provides a link to take corrective action.

If the Bidder has previously registered or been certified as a Small Business Enterprise, the Bidder should ensure it is currently registered and that its registration is active with the Division of Revenue and Enterprise Services, Small Business Registration and M/WBE Certification Services Unit, prior to the quote opening date, to be eligible for award.  The Bidder should ensure that it has completed the annual verification, if required.

Information, registration requirements and application are available at https://www.nj.gov/treasury/revenue/ucs.shtml.

## DISABLED VETERANS’ BUSINESS SET-ASIDE CONTRACT

Not applicable to this procurement.

## BID SECURITY

Not applicable to this procurement.

## BIDDER ADDITIONAL TERMS SUBMITTED WITH THE QUOTE

A Bidder may submit additional terms as part of its Quote.  Additional terms are Bidder-proposed terms or conditions that do not conflict with the scope of work required in this Bid Solicitation, the terms and conditions of this Bid Solicitation, or the State of New Jersey Standard Terms and Conditions.  Bidder proposed terms or conditions that conflict with those contained in the State of New Jersey Standard Terms and Conditions will render a Quote non-responsive.  It is incumbent upon the Bidder to identify and remove its conflicting proposed terms and conditions prior to Quote submission.

Quotes including Bidder proposed additional terms may be accepted, rejected, or negotiated, in whole or in part, at the State’s sole discretion.

If Bidder intends to propose terms and conditions that conflict with the State of New Jersey Standard Terms and Conditions, those Bidder proposed terms and conditions shall only be considered if submitted and agreed to pursuant to the electronic question and answer procedure.  Bidders shall not submit exceptions or modifications as part of the Quote or on the “Terms and Conditions” Tab through NJSTART.

## QUOTE CONTENT

The Quote should be submitted with the attachments organized in the following manner:

- Forms

- Bidder Quote Overview Form

- Bidder Data Sheet/Form

- State-Supplied Price Sheet

A Bidder should not password protect any submitted documents. Use of URLs in a Quote should be kept to a minimum and shall not be used to satisfy any material term of a Bid Solicitation. If a preprinted or other document included as part of the Quote contains a URL, a printed copy of the information should be provided and will be considered as part of the Quote.

## FORMS, REGISTRATIONS AND CERTIFICATIONS TO BE SUBMITTED WITH QUOTE

A Bidder is required to complete and submit the following forms.  As an alternative to uploading certain forms with the submitted Quote, a Bidder may complete several certifications electronically in NJSTART on the “Terms and Categories” Tab within the Vendor Profile.  Those forms that may be completed on the NJSTART “Terms and Categories” Tab are noted below. Additionally, a Bidder may attach completed forms to the Vendor Profile.  Refer to QRGs “Vendor Forms” and “Attaching Files” for additional instructions.  VENDOR QUICK REFERENCE GUIDES

### OFFER AND ACCEPTANCE PAGE

The Bidder should complete and submit the Offer and Acceptance Page with the Quote.  The Offer and Acceptance Page must be signed by an authorized representative of the Bidder.  If a Bidder does not submit the form with the Quote, the Bidder must comply within seven (7) Business Days of the State’s request or the State may deem the Quote non-responsive.

### OWNERSHIP DISCLOSURE FORM

Pursuant to N.J.S.A. 52:25-24.2, in the event the Bidder is a corporation, partnership or limited liability company, the Bidder must disclose all 10% or greater owners by (a) completing and submitting the Ownership Disclosure Form with the Quote; (b) if the Bidder has submitted a signed and accurate Ownership Disclosure Form dated and received no more than six (6) months prior to the Quote submission deadline for this procurement, the Division may rely upon that form; however, if there has been a change in ownership within the last six (6) months, a new Ownership Disclosure Form must be completed, signed and submitted with the Quote; or, (c) a Bidder with any direct or indirect parent entity which is publicly traded may submit the name and address of each publicly traded entity and the name and address of each person that holds a 10 percent or greater beneficial interest in the publicly traded entity as of the last annual filing with the federal Securities and Exchange Commission or the foreign equivalent, and, if there is any person that holds a 10 percent or greater beneficial interest, also shall submit links to the websites containing the last annual filings with the federal Securities and Exchange Commission or the foreign equivalent and the relevant page numbers of the filings that contain the information on each person that holds a 10 percent or greater beneficial interest. N.J.S.A. 52:25-24.2.

NOTE: In lieu of completing and submitting the paper-based form, the Bidder has the option to complete this form online in NJSTART on the “Terms and Categories” Tab.

A Bidder’s failure to submit the information required by N.J.S.A. 52:25-24.2 will result in the rejection of the Quote as non-responsive and preclude the award of a Contract to said Bidder.

### DISCLOSURE OF INVESTMENT ACTIVITIES IN IRAN FORM

The Bidder should  submit Disclosure of Investment Activities in Iran form to certify that, pursuant to N.J.S.A. 52:32-58, neither the Bidder, nor one (1) of its parents, subsidiaries, and/or affiliates (as defined in N.J.S.A. 52:32-56(e)(3)), is listed on the Department of the Treasury’s List of Persons or Entities Engaging in Prohibited Investment Activities in Iran and that neither the Bidder, nor one (1) of its parents, subsidiaries, and/or affiliates, is involved in any of the investment activities set forth in N.J.S.A. 52:32-56(f).  If the Bidder is unable to so certify, the Bidder shall provide a detailed and precise description of such activities as directed on the form.  If a Bidder does not submit the form with the Quote, the Bidder must comply within seven (7) Business Days of the State’s request or the State may deem the Quote non-responsive.

NOTE: In lieu of completing and submitting the paper-based form, the Bidder has the option to complete this certification online in NJSTART on the “Terms and Categories” Tab.

### DISCLOSURE OF INVESTIGATIONS AND OTHER ACTIONS INVOLVING BIDDER FORM

The Bidder should submit the Disclosure of Investigations and Other Actions Involving Bidder Form,  with its Quote, to provide a detailed description of any investigation, litigation, including administrative complaints or other administrative proceedings, involving any public sector clients during the past five (5) years, including the nature and status of the investigation, and, for any litigation, the caption of the action, a brief description of the action, the date of inception, current status, and, if applicable, disposition.  If a Bidder does not submit the form with the Quote, the Bidder must comply within seven (7) Business Days of the State’s request or the State may deem the Quote non-responsive.

NOTE: In lieu of completing and submitting the paper-based form, the Bidder has the option to complete this certification online in NJSTART on the “Terms and Categories” Tab.

### MACBRIDE PRINCIPLES FORM

The Bidder should submit the MacBride Principles Form.  Pursuant to N.J.S.A. 52:34-12.2, a Bidder is required to certify  that it either has no ongoing business activities in Northern Ireland and does not maintain a physical presence therein or that it will take lawful steps in good faith to conduct any business operations it has in Northern Ireland in accordance with the MacBride principles of nondiscrimination in employment as set forth in N.J.S.A. 52:18A-89.5 and in conformance with the United Kingdom’s Fair Employment (Northern Ireland) Act of 1989, and permit independent monitoring of their compliance with those principles.  If a Bidder does not submit the form with the Quote, the Bidder must comply within seven (7) Business Days of the State’s request or the State may deem the Quote non-responsive.

NOTE: In lieu of completing and submitting the paper-based form, the Bidder has the option to complete this certification online in NJSTART on the “Terms and Categories” Tab.

### SERVICE PERFORMANCE WITHIN THE UNITED STATES

The Bidder should submit a completed Source Disclosure Form. Pursuant to N.J.S.A. 52:34-13.2, all Contracts primarily for services shall be performed within the United States. If a Bidder does not submit the form with the Quote, the Bidder must comply within seven (7) Business Days of the State’s request or the State may deem the Quote non-responsive.

### CONFIDENTIALITY/COMMITMENT TO DEFEND

Pursuant to the New Jersey Open Public Records Act (OPRA), N.J.S.A. 47:1A-1 et seq., or the common law right to know, Quotes can be released to the public in accordance with N.J.A.C. 17:12-1.2(b) and (c).

The Bidder should submit a completed and signed Confidentiality/Commitment to Defend Form with the Quote.  In the event that the Bidder does not submit the Confidentiality form with the Quote, the State reserves the right to request that the Bidder submit the form after Quote submission.

After the opening of sealed Quotes, all information submitted by a Bidder in response to a Bid Solicitation is considered public information notwithstanding any disclaimers to the contrary submitted by a Bidder.  Proprietary, financial, security and confidential information may be exempt from public disclosure by OPRA and/or the common law when the Bidder has a good faith, legal/factual basis for such assertion.

When the Bid Solicitation contains a negotiation component, the Quote will not be subject to public disclosure until a notice of intent to award a Contract is announced.

As part of its Quote, a Bidder may request that portions of the Quote be exempt from public disclosure under OPRA and/or the common law. The Bidder must provide a detailed statement clearly identifying those sections of the Quote that it claims are exempt from production, and the legal and factual basis that supports said exemption(s) as a matter of law.  The State will not honor any attempts by a Bidder to designate its State-Supplied Price Sheet, Price List/Catalog, and/or the entire Quote as proprietary and/or confidential, and/or to claim copyright protection for its entire Quote.  If the State does not agree with a Bidder’s designation of proprietary and/or confidential information, the State will use commercially reasonable efforts to advise the Bidder. Copyright law does not prohibit access to a record which is otherwise available under OPRA.

The State reserves the right to make the determination as to what to disclose in response to an OPRA request.  Any information that the State determines to be exempt from disclosure under OPRA will be redacted.

In the event of any challenge to the Bidder’s assertion of confidentiality that is contrary to the State’s determination of confidentiality, the Bidder shall be solely responsible for defending its designation, but in doing so, all costs and expenses associated therewith shall be the responsibility of the Bidder. The State assumes no such responsibility or liability.

In order not to delay consideration of the Quote or the State’s response to a request for documents, the State requires that Bidder respond to any request regarding confidentiality markings within the timeframe designated in the State’s correspondence regarding confidentiality.  If no response is received by the designated date and time, the State will be permitted to release a copy of the Quote with the State making the determination regarding what may be proprietary or confidential.

### SUBCONTRACTOR UTILIZATION PLAN

Bidders intending to use Subcontractor(s) shall list all Subcontractors on the Subcontractor Utilization Plan form or may list the Subcontractor(s) on the “Subcontractor” Tab in NJSTART.

For a Quote that does NOT include the use of any Subcontractors, the Bidder is automatically certifying that, if selected for an award, the Bidder will be performing all work required by the Contract.

If it becomes necessary for the Contractor to substitute a Subcontractor, add a Subcontractor, or substitute its own staff for a Subcontractor, the Contractor will identify the proposed new Subcontractor or staff member(s) and the work to be performed.  The Contractor shall forward a written request to substitute or add a Subcontractor or to substitute its own staff for a Subcontractor to the State Contract Manager for consideration.    The Contractor must provide a completed Subcontractor Utilization Plan, a detailed justification documenting the necessity for the substitution or addition, and resumes of its proposed replacement staff or of the proposed Subcontractor’s management, supervisory, and other key personnel that demonstrate knowledge, ability and experience relevant to that part of the work which the Subcontractor is to undertake. The qualifications and experience of the replacement(s) must equal or exceed those of similar personnel proposed by the Contractor in its Quote.  The State Contract Manager will forward the request to the Director for approval.

NOTE: No substituted or additional Subcontractors are authorized to begin work until the Contractor has received written approval from the Director.

#### SMALL BUSINESS AND/OR DISABLED VETERANS’ BUSINESS SUBCONTRACTING SET-ASIDE CONTRACT

Not applicable to this procurement.

### RESERVED

Not applicable to this procurement.

### AFFIRMATIVE ACTION

The intended Contractor and its named Subcontractor(s) must submit a copy of a New Jersey Certificate of Employee Information Report, or a copy of Federal Letter of Approval verifying it is operating under a federally approved or sanctioned Affirmative Action program.  If the Contractor and/or its named Subcontractor(s) are not in possession of either a New Jersey Certificate of Employee Information Report or a Federal Letter of Approval, it/they must complete and submit the Affirmative Action Employee Information Report (AA-302).  Information, instruction and the application are available at https://www.state.nj.us/treasury/contract_compliance/index.shtml.

### RESERVED

Not applicable to this procurement.

### STATE OF NEW JERSEY SECURITY DUE DILIGENCE THIRD-PARTY INFORMATION SECURITY QUESTIONNAIRE

Not applicable to this procurement.

### BUSINESS REGISTRATION

In accordance with N.J.S.A. 52:32-44(b), a Bidder and its named Subcontractors must have a valid Business Registration Certificate (“BRC”) issued by the Department of the Treasury, Division of Revenue and Enterprise Services prior to the award of a Contract.  A Bidder should verify its Business Registration Certification Active status on the “Maintain Terms and Categories” Tab within its profile in NJSTART. In the event of an issue with a Bidder’s Business Registration Certification Active status, NJSTART provides a link to take corrective action.

### Certification of Non-Involvement in Prohibited Activities in Russia or Belarus Pursuant to P.L.2022, c.3

The Bidder should submit the Certification of Non-Involvement in Prohibited Activities in Russia or Belarus Form.  Pursuant to P.L.2022, c.3, a person or entity seeking to enter into or renew a contract for the provision of goods or services shall certify that it is not Engaging in Prohibited Activities in Russia or Belarus as defined by P.L.2002, c.3, sec. 1(e).  If a Bidder does not submit the form with the Quote, the Bidder must comply within seven (7) Business Days of the State’s request or the State may deem the Quote non-responsive.

## BIDDER QUOTE OVERVIEW FORM

The Bidder should submit the Bidder Quote Overview Form with its Quote. The Bidder should complete all of the information requested on the form, so that the State is able to evaluate the Bidder’s ability to complete the Scope of Work.  The Bidder’s responses to the questions on the form should demonstrate to the State that the Bidder’s plans and approach to complete the Scope of Work are realistic, attainable, appropriate, and that the Bidder’s Quote will lead to the successful completion of the tasks required.

## BIDDER DATA SHEET/FORM

The Bidder shall submit the Bidder Data Sheet with its Quote.  The Bidder Data Sheet will be used to evaluate the Bidder’s ability to complete the Scope of Work.

The Bidder should provide in its response to Part I of the Bidder Data Sheet all relevant information regarding its experience in successfully completing contracts of a similar size and scope to the work required by this Bid Solicitation.

The Bidder must provide, in Part II of the Bidder Data Sheet, details of any negative actions taken by other contracting entities against it in the course of performing these projects including, but not limited to, receipt of letters of potential default, default, cure notices, termination of services for cause, or other similar notifications/processes.  Additionally, the Bidder should provide details, including any negative audits, reports, or findings by any governmental agency for which the Bidder is/was the contractor on any contracts of similar scope.  In the event a Bidder neglects to include this information in its Quote, the Bidder’s omission of necessary disclosure information may be cause for rejection of the Bidder’s Quote by the State.

If proposing to use a Subcontractor, the Bidder should provide as an attachment to the Bidder Data Sheet documented experience to demonstrate that each Subcontractor has successfully performed work on contracts of a similar size and scope to the work that the Subcontractor is designated to perform in the Bidder’s Quote.  The Bidder must provide a detailed description of services to be provided by each Subcontractor.

## EXPERIENCE WITH CONTRACTS OF SIMILAR SIZE AND SCOPE

The Bidder should provide a comprehensive listing of contracts of similar size and scope that it has successfully completed, as evidence of the Bidder’s ability to successfully complete services similar to those required by this Bid Solicitation.  Emphasis should be placed on contracts that are similar in size and scope to the work required by this Bid Solicitation.  A description of all such contracts should be included and should show how such contracts relate to the ability of the firm to complete the services required by this Bid Solicitation.  For each such contract listed, the Bidder should provide two (2) names and telephone numbers of individuals for contracting party. Beginning and ending dates should also be given for each contract.

The Bidder must provide details of any negative actions taken by other contracting entities against them in the course of performing these projects including, but not limited to, receipt of letters of potential default, default, cure notices, termination of services for cause, or other similar notifications/processes.  Additionally, the Bidder should provide details, including any negative audits, reports, or findings by any governmental agency for which the Bidder is/was the contractor on any contracts of similar scope.  In the event a Bidder neglects to include this information in its Quote, the Bidder’s omission of this necessary disclosure information may be cause for rejection of the Bidder’s Quote by the State.

The Bidder should provide documented experience to demonstrate that each Subcontractor has successfully performed work on contracts of a similar size and scope to the work that the Subcontractor is designated to perform in the Bidder’s Quote.  The Bidder must provide a detailed description of services to be provided by each Subcontractor.

## PUBLIC WORKS CONTRACTOR REGISTRATION

At the time of the Quote due date, the Bidder and Subcontractors performing public work as defined in N.J.S.A. 34:11-56.26 must be registered in accordance with the Public Works Contractor Registration Act (PWCRA), N.J.S.A. 34:11-56.48 et seq.  This registration is required for all trade categories required to perform work as listed herein.

Questions regarding Public Works Contractor Registration should be addressed to:

Contractor Registration

New Jersey Department of Labor and Workforce Development Division of Wage and Hour Compliance

PO Box 369 Trenton, NJ 08625-0389

Tel. 609-292-9464

Fax: 609-633-8591

For additional information, please reference the following web site:

https://www.nj.gov/labor/wagehour/regperm/pw_cont_reg.html.

NOTE:	 All Bidders and Subcontractors performing public work must be registered at the time of Bid Opening. The Bidder should provide proof of registration on the date of Bid Opening. Failure for all Bidders and Subcontractors to be registered in accordance with the Public Works Contractor Registration Act at the time of Quote opening, shall result in the Quote being deemed non-responsive.

## FINANCIAL CAPABILITY OF THE BIDDER

The Bidder should provide sufficient financial information to enable the State to assess the financial strength and creditworthiness of the Bidder and its ability to undertake and successfully complete the Contract.  In order to provide the State with the ability to evaluate the Bidder’s financial capacity and capability to undertake and successfully complete the Contract, the Bidder should submit the following:

- For publicly traded companies the Bidder should provide copies or the electronic location of the annual reports filed for the two most recent years; or

- For privately held companies the Bidder should provide the certified financial statement (audited or reviewed) in accordance with applicable standards by an independent Certified Public Accountant, including a balance sheet, income statement, and statement of cash flow, and all applicable notes for the most recent calendar year or the Bidder’s most recent fiscal year.

If the information is not supplied with the Quote, the State may still require the Bidder to submit it.  If the Bidder fails to comply with the request within seven (7) Business Days, the State may deem the Quote non-responsive.

A Bidder may designate specific financial information as not subject to disclosure when the Bidder has a good faith legal/factual basis for such assertion.  The State reserves the right to make the determination to accept the assertion and will so advise the Bidder.

## STATE-SUPPLIED PRICE SHEET INSTRUCTIONS

The Bidder must submit its pricing using the State-Supplied Price Sheet accompanying this Bid Solicitation and located on the “Attachments” Tab.

There are fifty-two (52) price lines, which are grouped and itemized as follows:

| Group Number | Price Line Numbers |
| --- | --- |
| Group 1 – North Region | 1 - 13 |
| Group 2 – Central Region | 14 - 26 |
| Group 3 – South Region | 27 - 39 |
| Group 4 – Capitol Complex | 40 - 52 |

Each of the four (4) regions contains the same thirteen (13) price lines, divided as follows:

| Price Line | Service | Unit of Measure |
| --- | --- | --- |
| 1 | Mechanic - Regular Rate | Hour |
| 2 | Mechanic - Overtime Rate | Hour |
| 3 | Mechanic - Premium Rate | Hour |
| 4 | Helper - Regular Rate | Hour |
| 5 | Helper - Overtime Rate | Hour |
| 6 | Helper - Premium Rate | Hour |
| 7 | Adjuster - Regular Rate | Hour |
| 8 | Adjuster - Overtime Rate | Hour |
| 9 | Adjuster - Premium Rate | Hour |
| 10 | Team - Regular Rate | Hour |
| 11 | Team - Overtime Rate | Hour |
| 12 | Team - Premium Rate | Hour |
| 13 | % markup for materials/supplies (not to exceed 10%) | Percentage |

Bidders are able to Bid on one (1) group, all groups, or any combination thereof.  Bidders must bid on the first twelve (12) price lines contained within a group (Group 1 Price Lines 1 – 12; Group 2 Price Lines 14-25; Group 3 Price Lines 27-38; Group 4 Price Lines 40-51) to be responsive for that group. Bidders may bid on the thirteenth (13th) price line in a group (Group 1 Price Line 13; Group 2 Price Line 26; Group 3 Price Line 39; Group 4 Price Line 52). If a Bidder does not bid on the first twelve (12) price lines within a group, its Quote will be considered non-responsive for that group only.

The State intends to award one (1) or more Contracts per group (Group 1 – North Region, Group 2 – Central Region, Group 3 – South Region, and Group 4 – Capitol Complex), in accordance with Section 8.16 of this Bid Solicitation. Each region may have up to six (6) Contracts. Using Agencies will be able to utilize the awarded Contractors per group following the methodology demonstrated in Bid Solicitation Section 4.21, Method of Operation.

Price line items are grouped for Quote evaluation purposes only.  Upon Contract award, Using Agencies will be able to order any price lines within the group individually.

Any price changes including hand written revisions or "white-outs" must be initialed.  Failure to initial price changes shall preclude a Contract award from being made to the Bidder pursuant to N.J.A.C. 17:12-2.2(a)(8).

Markup of Parts (Price Lines 13, 26, 39, and 52) is a markup over cost for all repair parts and material per group. For purposes of this Bid Solicitation, the markup for repair parts cannot exceed 10% above the Contractor’s cost. Any Bidder who offers a markup over 10% will be nonresponsive and therefore, not eligible for an award for that Group.

### BID-SPECIFIC STATE-SUPPLIED PRICE SHEET INSTRUCTIONS

- Step 1 - The Bidder should enter the Bidder name in the field titled “Bidder Name:” and the date in the field titled “Date:” located at the top of the State-Supplied Price Sheet

- Step 2 – If the Bidder would like to provide a bid for Group 1, comprised of Price Lines 1-13, it shall provide a Firm Fixed Price in US dollars in the corresponding column titled “Unit Pricing” on the State-Supplied Price Sheet for lines 1-12 within the group. This Firm Fixed Pricing shall be an All-Inclusive Loaded Hourly Rate as defined in Bid Solicitation Section 9.3. For Price line 13, the Bidder may insert a number percent mark up for materials and supplies. Mark up for parts cannot exceed 10% above the Contractor’s cost. If the Bidder is not marking up the cost for materials and supplies (Price Line 13), the bidder should enter “0” in this price line. Any Bidder who offers a markup over 10% on Price Line 13 will be nonresponsive and therefore, not eligible for an award for that Group. Any bidder who leaves price line 13 blank shall be considered to have submitted a quote of “0%” for that line.

- Step 3 – If the Bidder would like to provide a bid for Group 2, comprised of Price Lines 14-26, it shall provide a Firm Fixed Price in US dollars in the corresponding column titled “Unit Pricing” on the State-Supplied Price Sheet for lines 14-25 within the group. This Firm Fixed Pricing shall be an All-Inclusive Loaded Hourly Rate as defined in Bid Solicitation Section 9.3. For Price line 26, the Bidder may insert a percent mark up for materials and supplies. Mark up for parts cannot exceed 10% above the Contractor’s cost. If the Bidder is not marking up the cost for materials and supplies (Price Line 26), the bidder should enter “0” in this price line. Any Bidder who offers a markup over 10% on Price Line 26 will be nonresponsive and therefore, not eligible for an award for that Group. Any bidder who leaves price line 26 blank shall be considered to have submitted a quote of “0%” for that line.

- Step 4 – If the Bidder would like to provide a bid for Group 3, comprised of Price Lines 27-39, it shall provide a Firm Fixed Price in US dollars in the corresponding column titled “Unit Pricing” on the State-Supplied Price Sheet for lines 27-38 within the group. This Firm Fixed Pricing shall be an All-Inclusive Loaded Hourly Rate as defined in Bid Solicitation Section 9.3. For Price line 39, the Bidder may insert a percent mark up for materials and supplies. Mark up for parts cannot exceed 10% above the Contractor’s cost. If the Bidder is not marking up the cost for materials and supplies (Price Line 39), the bidder should enter “0” in this price line. Any Bidder who offers a markup over 10% on Price Line 39 will be nonresponsive and therefore, not eligible for an award for that Group. Any bidder who leaves price line 39 blank shall be considered to have submitted a quote of “0%” for that line

- Step 5 – If the Bidder would like to provide a bid for Group 4, comprised of Price Lines 40-52, it shall provide a Firm Fixed Price in US dollars in the corresponding column titled “Unit Pricing” on the State-Supplied Price Sheet for lines 40-51 within the group. This Firm Fixed Pricing shall be an All-Inclusive Loaded Hourly Rate as defined in Bid Solicitation Section 9.3. For Price line 52, the Bidder may insert a percent mark up for materials and supplies. Mark up for parts cannot exceed 10% above the Contractor’s cost. If the Bidder is not marking up the cost for materials and supplies (Price Line 52), the bidder should enter “0” in this price line. Any Bidder who offers a markup over 10% on Price Line 52 will be nonresponsive and therefore, not eligible for an award for that Group. Any bidder who leaves price line 52 blank shall be considered to have submitted a quote of “0%” for that line.

### USE OF “NO BID” VERSUS “NO CHARGE” ON THE STATE-SUPPLIED PRICE SHEET

All price lines must be filled out in accordance with the instructions above.  If the Bidder is not submitting a price for an item on a price line, the Bidder must indicate “No Bid” on the State-Supplied Price Sheet accompanying this Bid Solicitation. Bidders are cautioned that submitting “No Bid” for a required price line or group will result in the Quote being deemed non-responsive for the required price line or group. If the Bidder will supply an item on a price line free of charge, the Bidder must indicate “No Charge” on the State-Supplied Price Sheet accompanying this Bid Solicitation.  The use of any other identifier may result in the Bidder’s Quote being deemed non-responsive.

# SCOPE OF WORK

The Contractor shall provide full service preventative maintenance, repair, testing, and inspection for all items necessary for the proper operation and functionality of all Vertical Transportation Equipment (VTE). All references to VTE included herein shall be considered to include elevators, escalators, lifts, dumbwaiters, hoists, and moving walkways. Any additional items may be added as necessary.

The State shall reserve the right to add or delete locations at any time during the Contract term.

## CONTRACTOR REQUIREMENTS

The Contractor shall, at a minimum:

- Perform all maintenance and repairs on site unless granted permission by the State Building Manager (SBM) to remove equipment for off-site repair;

- Employ qualified, trained, skilled and competent personnel to perform work promptly and in accordance with a schedule as approved by the Using Agency. Mechanics must have a minimum of five (5) years of experience as a mechanic. The mechanics and supervisory personnel shall have experience in the maintenance of these particular types of VTE. The Contractor shall provide the SBM with the resumes of any new employee hired during the Contract period, including extensions;

- Provide unlimited call-back maintenance service during normal business hours;

- Perform an existing deficiency inspection and develop a deficiency list for each building. The deficiency list must be submitted to the SBM within sixty (60) days after the receipt of a Purchase Order from the Using Agency. The SBM and assigned representatives will review the listing submitted and will have final say on the determination of the application deficiency and related costs. If a deficiency list is not submitted the Contractor shall bear all repair/maintenance costs;

- Notify the SBM of the existence or development of any defects in, or repairs to, the equipment which it does not consider to be its responsibility under the terms of this Contract. The Contractor shall furnish the Using Agency with a written estimate of the cost to correct any such defects or make the required repairs. The written estimate of the repairs is to include the delivery of services date and is required within 48 hours of notification to SBM. The Using Agency reserves the right to make the final determination concerning the responsibility of such defects, correction, or repairs;

- The Contractor will not be required to make repairs at its expense due to negligence or misuse of the equipment by persons other than the Contractor. A written report with photos of such alleged negligence or misuse shall be submitted to the SBM immediately. The Using Agency reserves the right to make the final determination concerning the responsibility of such defects, correction or repairs;

- Give immediate notice to the SBM of any condition which may present a hazard to either the equipment or passengers, and repair the condition as soon as scheduling can be arranged. If the condition is deemed a safety hazard, the Contractor shall make repairs to the equipment as soon as possible and provide guidance and recommendations to the SBM until it is fixed;

- If requested by the SBM, the Contractor shall hold meetings with the SBM that shall result in status reports on all maintenance and repair issues; and

- Designate a Project Manager, subject to approval by the SBM. The Project Manager will have sufficient delegated authority  so as to be able to exercise day-to-day decision making on all operations and business matters, relating to the Contractor’s performance of this Contract.

  - The Project Manager shall:

    - Have the responsibility of directing and coordinating the Contractor’s performance of the requirements in this Contract;

    - Serve as the Contractor’s liaison with the Using Agencies; and

    - Attend assessment meetings with the Using Agencies as requested.

## SERVICE HOURS

All maintenance is to be performed during regular business hours, 8:00 AM – 4:30 PM, Monday through Friday, excluding holidays set forth in Bid Solicitation Section 4.2.3, unless other scheduled times are approved in advanced by the SBM.

### HOURLY LABOR REPAIR RATES

All hourly labor rates shall be an All-Inclusive Loaded Hourly Rate. The following work hours shall apply to this Contract:

- Regular Hourly Rate: Work performed between 8:00 AM to 4:30 PM, Monday through Friday excluding holidays listed in Section 4.2.3 of this Bid Solicitation;

- Overtime Hours: Pay rate for work performed on Saturday or before or after regular work hours, Monday through Friday. Overtime Pay shall be in accordance with New Jersey Department of Labor & Workforce Development (DLWD) prevailing wage rate guidelines.

- Premium Time Hours: The additional payment above the prevailing hourly wage paid for night, evening differentials, Sundays and/or holiday pay. Premium Pay shall be in accordance with DLWD prevailing wage rate guidelines.

### OVERTIME PAY RATE

During the term of the Contract, the State may authorize overtime hours for the Contractor in order to expedite major repairs. This authorization will be granted only in those instances where the Using Agency has made a determination that such action in the best interests of the State.

### PREMIUM PAY RATE

For payment purposes, only the following days listed below will be treated as Holiday/Premium pay rate for hours requested and required by the State. Work performed on all other State Holidays or State Paid Days Off, such as snow days, will be treated as regular work days. Any hours worked by the Contractor to be billed at an hourly rate on these regular work days will be paid at straight hourly rates.

- New Year's Day;

- Memorial Day;

- July 4th (Independence Day);

- Labor Day;

- Veteran's Day;

- Thanksgiving Day; and

- Christmas Day.

These recognized holidays are subject to change based upon Legislative approval or other directives. Should a holiday fall on a weekend, the day designated by the State shall be recognized as the holiday.

### SIGN-IN/SIGN-OUT PROCEDURE

The Contractor’s personnel must observe all regulations in effect at the designated location, including security sign-in/sign-out procedures. While on State property, employees must follow all State rules and regulations as well as those of each building in which they are working in.

The above mentioned sign-in procedure and sign-in sheet will be the official record of employees for all purposes of this Contract. This shall be used by the SBM for Contractor employee and work verification purposes.

## CALLBACK SERVICE

The Contractor shall meet the following callback service requirements:

- The Contractor must be accessible by telephone 24 hours per day, seven (7) days per week, 365 days a year to receive service calls from Using Agencies and to dispatch those calls to their staff to be on site within one (1) hour during regular working hours and within two (2) hours during overtime or premium hours of the call;

- Emergency callback service requires the Contractor to report to the site of the emergency within thirty (30) minutes after receipt of request. An emergency situation may mean when an individual is trapped inside an elevator, or the existence of any other clear and present danger to health and safety; and

- The callback service shall be limited to adjustment or repairs to provide uninterrupted elevator service. There shall be no additional charge for callback service during regular working hours.

## MAINTENANCE RESPONSIBILITIES

The Contractor shall provide the minimum maintenance service as specified per the type of VTE. Maintenance shall provide a constant, high quality service to properly protect all equipment from deterioration and to provide constant peak performance of all VTE’s, resulting in a minimum of down time for any portion of the system.

- No more than one (1) elevator per bank shall be out of service at one time for routine scheduled maintenance. The time of day that each elevator can be shut down for routine maintenance shall be scheduled with the SBM to minimize disruption. If the elevator will be out of service for more than four (4) hours, the Contractor must notify the SBM in advance and secure approval prior to commencing with the work;

- At any point during the term of this Contract, but no later than 2 months prior to the end of the Contract Term, the Using Agency may make thorough maintenance audits of all equipment covered under this Contract. At the conclusion of such audits, the Using Agency shall give the Contractor written notice of any deficiency found. The Contractor shall be responsible for correction of these deficiencies within 30 days after receipt of such notice. Nothing in this paragraph absolves Contractor of its responsibilities to make repairs during the entire Contract term to ensure safe operation of all VTE;

- Contractor shall be responsible for providing all services, materials, labor, supplies, tools and equipment necessary to:

      - Maintain all VTE and associated equipment in a safe, clean, quiet, and smooth riding condition;

      - Maintain an inventory on site or in vehicle of all the commonly replaceable parts necessary to repair, clean, and service VTE;

      - Repair or replace any malfunctioning part. There shall be no exception for parts considered to be obsolete;

      - Maintain elevator monitoring systems;

      - Perform equipment examination at the intervals specified for each VTE;

      - Perform all inspections and maintenance operation as specified in ASME A17.1 (Safety Codes for Elevators and Escalators) and A17.2 (Guide for Inspection of Elevators, Escalators, and Moving Walks) including current addenda and interpretations;

      - Perform all tests required by regulations and to meet ASME A17.1 and following A17.2 including current addenda and interpretations; and

      - Ensure performance with door operation, landing accuracy and rated speed compliance within the established manufacturer’s guidelines. Complete all repairs and corrections required by the annual inspection report to meet the compliance date on the report. The Contractor shall be responsible for all re-inspection fees for failure of initial annual inspection due to Contractor non-compliance.

- If any VTE is not functioning properly when the Contractor leaves the service site they must inform the SBM and give its estimate timeline of when the repair will be completed;

- Service tickets must be submitted to the SBM of the building where the elevator was serviced. Service tickets must show the date, time in and out, explanation of the elevator problem or work being done, and the status of the work when leaving the site. Tickets must be submitted physically and electronically;

- The Contractor shall also examine and make necessary adjustments or repairs to the accessory equipment, including re-lamping of signal equipment, hall lanterns car and corridor position indicators, car stations, traffic director station, electric door operators, intercom systems, interlocks, door hangers, and safety edges;

- All replacement parts shall be new and specifically designed for the VTE on which they are to be used. All old parts must be returned to the SBM upon completion of repairs, unless otherwise requested by the SBM;

- The Contractor shall furnish and use lubricants as recommended by the original manufacturer of the equipment or an approved equal. The Contractor shall keep record and notify the SBM of excessive oil use for Hydraulic VTEs;

- The Contractor shall be responsible for keeping the exterior of the VTE and any other parts of the equipment, painted with heat resistant enamel and presentable at all times. The motor windings shall be treated as needed, with proper insulating compound as recommended by the motor manufacturer. Cleaning and refinishing of the interior of the cars and exterior of hoistway door frames are excluded from this Contract;

- The Contractor shall maintain all VTE within enclosures, pits, machine rooms, and the assigned Contractor work space is to be kept clean and orderly, free of dirt, dust and debris, pits and machine spaces shall be kept dry and clean. The Contractor shall be responsible for disposal of all waste in accordance with local, State and federal requirements;

- The Contractor shall not be required to install new attachments on the VTE whether or not recommended or directed by insurance companies or by governmental authorities, nor make any replacements with parts of a different design. The Contractor shall not be required to make renewals or repairs necessitated by reason of negligence or misuse of the equipment or by reason of any other cause beyond the Contractor's control except ordinary wear and tear unless the Contractor receives just compensation;

- The Contractor shall supply and install any and all group/control system software upgrades at no additional charge, for the term of the Contract;

- The Contractor shall keep the VTE maintained to operate at the original contract speed, keeping the original performance times, including acceleration and retardation as designed and installed by the manufacturer. The door operation shall be adjusted as required to maintain the original door opening and door closing times, within legal limits;

- The Contractor shall immediately notify the SBM when any parts or components within the elevator system may require repair, modification or replacement. Should a failure to or in the elevator system occur because the Contractor did not notify the SBM, the Contractor shall be liable for any and all costs incurred by the State to return the elevator to its original safe operating condition;

- The Contractor shall immediately notify the SBM of any safety hazards as soon as possible. In the event of a safety hazard, the Contractor shall make immediate repairs to the equipment and provide guidance and recommendations to the SBM until it is fixed ;

- If the level of the Contractor’s performance is questioned by the State, a third party hired by the State may be called in to inspect and to verify possible negligence on the part of the Contractor. If the alleged negligence is verified, the costs of such inspection and corrective-action shall be borne by the Contractor; and

- The Contractor shall not be responsible for the following:

  - Repairing, refinishing or replacement of cab enclosures, cab floors, cab door panels, light fixtures and lamps, hoist-way door panels, frames and sills, hydraulic cylinders, card readers or other access control devices, smoke/fire alarms and detectors, fireman phones, telephone service, intercom or music systems, air conditioner or heaters, pit pumps and alarms, main power disconnect switches and feeder to the controller; (NOTE: Contractor will be responsible for sills if the door guides have not been properly maintained);

  - The costs of materials and labor for the installation of any new attachments or features; and

  - Parts or items damaged or made defective by misuse, fire, water, theft, Force Majeure.

## ADDITIONAL SERVICES

The following services may be requested by the Using Agency at which the Contractor will be reimbursed at the hourly rates on the State Supplied Price Schedule:

- Any repairing, resetting, adjusting or replacing elevator components or associated equipment necessary resulting from misuse, fire, water, or theft;

- Repair or replace elevator components excluded from Section 4.4 (Q) of this Bid Solicitation; and

- Services to improve or upgrade elevator components at the State’s request.

## MAINTENANCE SCHEDULE

The Contractor shall provide the minimum preventative maintenance for all Using Agency’s equipment specified herein. If specific equipment covered by this Contract requires additional preventative maintenance for safe reliable operation, as specified by the manufacturer, the Contractor shall perform the required additional preventative maintenance without added cost to the State.

### GEARLESS, GEARED, AND HYDRAULIC ELEVATORS

- Gearless Elevators - Contractor shall provide a minimum of three (3) on-site hours per elevator/per month exclusively for preventive maintenance;

- Geared Elevators - Contractor shall provide a minimum of two (2) on-site hours per elevator/per month exclusively for preventive maintenance; and

- Hydraulic Elevators – Contractor shall provide a minimum of one (1) on-site hours per elevator/per month exclusively for preventive maintenance.

Callbacks, repairs, inspections and clean-downs are not to be included in these hours.

#### MONTHLY MAINTENANCE

The Contractor shall provide monthly maintenance on the following (note: this list is subject to change):

- Traction Machine: All bearings, drive sheave, and other machine components;

- Brake pulley, brake coil, brake pins, brake contacts, linings and other brake components;

- Motor windings, rotating elements, commutators, brushes, brush holders, bearings and field coils;

- Hoist cables, governor cables, compensating cables and compensating chains, including adjustment of tension on all cables;

- Car safety mechanism and load weighing equipment;

- Controller equipment: All components including all relays, solid state components, resistors, condensers, transformers, contacts, leads, computer devices, selector switches, mechanical or electrical driving equipment, coils, magnet frames, contact switch assemblies, springs, solenoids, resistance grids, hoistway vanes, magnets and inductors;

- Governor: Including governor sheave, shaft assembly gears, bearing contacts, jaws and pit tension assembly;

- Sheaves: Including defector, secondary, compensating sheaves, shafts, bearings, grease retainers, compensation sheave frame, contacts and hold down devices;

- Hoistway door operators, interlocks or locks and contacts, hoistway door hangers, tracks, bottom door gibs, cams, rollers and auxiliary door closing devices for power operated doors;

- Hoistway limit switches, slowdown switches, leveling switches and associated cams, vanes and electronic components;

- Guide shoes assemblies including rollers;

- Perform general inspection of machinery, pumps, piping, drives, valves, selector or floor controllers;

- Empty drip pans, discard oil, check reservoir oil level;

- Inspect and lubricate machinery, contacts, linkage and gearing;

- Ride the car and check all components to insure proper operation;

- If rails are lubricated, check condition and lubrication.  Service lubricators;

- Replace all burned out lamps in elevator car, machine room equipment;

- Clean trash from pit and empty drip pans, discard oil. Examine plunger seals and correct excess leakage;

- Observe operation of elevator throughout its full range and at all floors it serves to observe operation of doors, reopening devices and performance. Test controls, safety devices, leveling, re-leveling, and other devices. Any deficiencies discovered require that the Contractor determine cause and implement corrective action;

- Check door operation, clean, lubricate and adjust brakes, checks, linkages, gears, wiring motors, check keys, set screws, contacts, chains and cams;

- Make needed repairs to any intercommunication system, normal and emergency lights, fan, emergency call system or alarm, car station;

- Inspect hoistway and pit. Clean and lubricate equipment as required. Service guide rail lubricators;

- Observe operation of motor and pump, oil lines, tank, controls, plunger, packing, etc. Adjust or repair as required;

- Check packing glands of valves and cylinder and tighten to prevent loss of fluids;

- Visually inspect controller, contacts and relay. Check adjustment and replace contacts as required; and

- Observe operation of signal system used.

#### QUARTERLY MAINTENANCE

The Contractor shall provide quarterly maintenance on the following (note: this list is subject to change):

- Check leveling operation. Clean and adjust leveling switches, hoistway vanes, magnets, and inductors. Repair and/or adjust for proper leveling;

- Check hoistway doors. Clean, lubricate, and adjust tracks, hangers and up thrust eccentrics, linkage gibs and interlocks; and

- Clean, adjust, and lubricate car door or gate tracks, pivots, and hangers.

#### SEMI-ANNUAL MAINTENANCE

The Contractor shall provide semi-annual maintenance on the following (note: this list is subject to change):

- Check controllers. Clean with blower check alignment of switches, relays, timers, contacts, hinge pins, etc., adjust and lubricate. Check all resistance tubes and grids. Check oil in overload relays, settings and operation of overloads. Clean and inspect fuses and holders and all controller connections. Check and adjust all electronic components;

- In hoistway examine guide rails, cams and fastenings. Inspect and test limit and terminal switches. Check and adjust car shoes, gibs or roller guides. Adjust or replace as required;

- Clean all overhead beams, sills, bottom of platform and car tops;

- Clean car light fixture or luminous ceiling panel;

- On tape drives check hitches and broken tape switch;

- Check car stile channels for bends or cracks: also car frame, cams, supports and car steadying plates;

- Lubricate guide shoe stems;

- Check governor and tape tension sheave fastenings; and

- Check fastenings and operation of door checks, interlocks clean and lubricate pivot points as required.

#### ANNUAL MAINTENANCE

The Contractor shall provide annual maintenance on the following (note: this list is subject to change):

- Thoroughly clean car guide rails using a non-flammable or high flash point solvent to remove lint, dust and excess lubricant;

- Take a sample of hydraulic fluid and have tested by certified laboratory for viscosity, color, contamination, foaming and other properties specified by the equipment manufacturers. Drain and replace fluid if it fails to meet manufacturer’s specified properties;

- Thoroughly clean the mechanism, pit, top and bottom of car, etc; and

- Perform all annual tests as required by ASME A17.1.

### ESCALATORS

The Contractor shall provide a minimum of four (4) on-site hours per escalator/per month exclusively for preventive maintenance. Callbacks, repairs, inspections and clean-downs are not to be included in these hours.

#### BI-WEEKLY MAINTENANCE

The Contractor shall examine, adjust, lubricate, clean, and when conditions warrant, repair or replace the following items and all other mechanical or electrical equipment on a bi-weekly basis:

- Machines, Worm gears, gears, external gears, drive chains, thrust bearings, main bearings and other machine components;

- Drive motors, gear reducers, stub shafts, sprocket bearings, drive chains and brake assemblies;

- Handrail, handrail drive chains, handrail brush guards, handrail guide rollers, and alignment devices;

- Rack sections & bushings, step axles, axle rollers and side rollers;

- Steps, step treads, step wheels, step chains, step axle, tracks and bushings;

- Controllers: All components including relays, electronic components, contacts, solid state components, resistors, condensers, transformers, leads, mechanical and electrical timing devices along with any and all computer devices; and

- Balustrade, skirt panels, demarcation lighting, skirt brush assembles comb-plates, floor plates and all safety device assemblies.

- Any other items as determined by the SBM or Using Agency

#### QUARTERLY MAINTENANCE

The Contractor shall provide quarterly maintenance on the following (note: this list is subject to change):

- Upper drives, upper drive bearings, tension sprocket bearings, upper and lower newel bearings;

- Brake pulley, brake coil, brake pins, brake contacts, linings and other brake components;

- Motor, motor windings, rotating elements, and bearings;

- Controllers, components including all relays, solid state components, resistors, condensers, transformers, contacts, leads, computer devices, mechanical or electrical driving equipment, coils, magnet frames, contact switch assemblies, springs, solenoids, resistance grids, and operating rectifiers; and

- All safety device switches and lighting features.

#### ANNUAL MAINTENANCE

The Contractor shall provide annual maintenance on the following (note: this list is subject to change):

- Examine all safety devices and conduct the routine and periodic inspections as required. All tests shall be performed in accordance with the provisions of the American National Standard, Safety Code for Elevators and Escalators (ASME A17.1 and ASME A17.2);

- Full clean down of each escalator, by removal of at least half of the steps, clean out pits, pans and all steps surfaces. Escalators clean-downs are limited to being out of service for two (2) days. Any overtime that may be required to complete this work is included in the monthly cost;

- Furnish lubricants compounded specifically for escalator usage;

- It is the intent of this Contract to provide for complete maintenance of the State’s escalators so that they shall be in first class operating condition at all times. ASME A17.1 as revised and amended, shall govern except where a more stringent code, a code having legal jurisdiction, or these Contract provisions include more rigid requirements. Inspections shall be carried out in accordance with ASME A17.2. Work not particularly specified in the Contract, but involved in carrying out the intent of complete and proper execution of the work may be required, and shall be performed by the Contractor. The apparent silence of the Contract as to any detail, or the apparent omission from them of any work to be done and only the best general practice is to prevail and that only the best materials and workmanship is to be used. Interpretation of the Contract shall be made upon that basis;

- The Contractor agrees that when an escalator is shut down or fails to operate that it will return the equipment to service with as little delay as possible. When an escalator is shut down or fails to operate, the Contractor shall place a sign in full view and on a barrier placed at the foot of the escalator, indicating that the escalator is "Temporarily Out of Order". The sign shall also include the approximate time and/or date at which the escalator is expected to be back in service;

- The State, at all times, has the right to make inspections of escalators and the work of the Contractor, and the Contractor agrees to perform maintenance work and make repairs deemed necessary by the State. The Contractor also agrees to provide the necessary labor to perform these inspections at no extra cost to the State;

- The escalator shall be kept in first class operating condition maintaining the same speeds, safety, and efficiency as specified in the original escalator maintenance manual. Proper safety devices and safety requirements, in accordance with all applicable codes in ASME A17.1, shall be followed, with inspections performed according to ASME A17.2; and

- Written records of types of inspections repairs etc. to be furnished to the SBM within two (2) weeks of the date of the work.

## NJDOT MOVEABLE BRIDGE ELEVATOR REQUIREMENTS

It is required that all moveable bridge elevators be inspected on a monthly basis. Prior to the inspection, the Contractor is required to notify the NJDOT SBM forty-eight (48) hours in advance to any work commencing under this Bid Solicitation.

The Contractor is required to do the following:

- Document all findings and test results in a narrative form; the deficiencies should be documented on a separate form with a cost associated to each item to complete the repair. Once the inspection is complete, the reports become the property of the NJDOT;

- Have available the required testing equipment such as pressure gauges, multi-meters, amp-meters, and other specialized equipment used during elevator inspections;

- Clean and lubricate the elevator components that control the mechanical operation and speed of the elevator;

- Test electrical wiring, control boxes, electrical circuits, and operating controls must be tested for proper operation as per the manufacturer’s recommendations;

- Re-tighten the connections should any loose connections be found;

- Check elevators for proper speed as required by the manufacturer;

- Test emergency telephones located on the elevators will be checked for proper operation;

- Inspect and test elevator doors for proper operation; and

- Test and inspect floor-to floor travel, acceleration and deceleration of the elevator, and emergency and safety equipment.

## SAFETY INSPECTION AND TESTS

All services, repair and inspection shall be in compliance with the State of New Jersey Uniform Construction Code (UCC), and all referenced codes and subcodes applicable during the term of the Contract. Routine and period testing and inspection shall be performed and meet all specifications as specified in the latest edition of ASME A.17.1, Part 8 Section 8.11 Periodic Inspections and Witnessing of Tests as specified below and is subject to change:

- One Year Testing and Inspection: The Contractor shall, at intervals of no longer than one (1) year from the Contract start date, perform the Routine Testing and Inspection as outlined in ASME A17.1, Part 8, Section 8.11. NOTE: The elevators on the NJDOT bridges require annual inspections to be conducted with the assistance of NJDOT personnel.

- Five Year Testing and Inspection: The Contractor shall, at intervals of no longer than five (5) years from the Contract start date, perform the Routine Testing and Inspection as outlined in ASME A17.1, Part 8, Section 8.11. The tests shall be conducted in the presence of the State of New Jersey designated Elevator inspector.

- After completion of the requested safety test, the Contractor shall submit a written document indicating the applicable test information. The Contractor may use the standard form or checklist per ASME 17.1.

- After tests have been performed, all safety devices shall be checked and adjusted as required to meet manufacturer’s recommendations. Metal test tags shall be affixed to all equipment as required by code and stamped with the appropriate information. Cars shall not be placed into service until all tests, checks and adjustments are complete and VTEs are in proper working condition.

- The Contractor shall coordinate the annual elevator State test of smoke detector and emergency generator systems with the State electrician, smoke detector Contractor and emergency generator Contractors. In order to meet the requirements of the test, the State shall be responsible for any costs associated with the said electrician, smoke detector and emergency generator Contractors.

- The Contractor shall supply the State the use of contractor personnel to conduct code mandated inspections at no additional cost. Personnel must be prepared to conduct ASME A17.2 inspections for VTE covered by this agreement in accordance with ASME A17.1.

## PARTS AND MATERIALS

The Contractor shall provide all parts and materials required to perform the work described in these specifications (note: this list is subject to change):

- Contractor must have access at all times, for immediate delivery and installation a sufficient supply of emergency spare parts for repairs. Standard repair and maintenance parts must be kept in stock at the building being serviced;

- Contractor must have access to replacement parts for drive motors, drives and machines available for replacement within 48 hours; and

- All replacement parts shall be new, of the best quality and suitable for their intended use. Parts must be obtained from the original manufacturer. Equivalent parts may be used only if approved by the using agency in writing. All parts requiring repair shall be rebuilt to “like new” condition.

### PURCHASE OF PARTS AND MATERIALS

Repair and replacement of parts and materials shall be provided by the Contractor under this Contract. The Contractor shall have available the type of inventory required to service and repair all systems, as well as the ability to purchase parts and materials from suppliers when needed.

The Contractor shall obtain competitive pricing for parts and materials when such purchases are required, unless otherwise approved by the SBM. The Contractor shall always select the most cost advantageous parts and materials required to successfully replace and/or repair, unless otherwise approved by the SBM.

The Contractor is encouraged to provide a discount on parts and materials whenever possible; however, mark-ups on parts costs shall not exceed the awarded markup percentage, which shall not exceed 10%, and should represent the fair market value. All markups shall be based upon the price paid by the Contractor.  All shipping costs are considered to be part of the overall cost. Reimbursement will be provided only upon submission of supplier's invoice.

The Contractor is reminded that an audit of their supply invoices and all other documents may be undertaken not only during the Contract period, but also for a period of up to five (5) years beyond the completion of the Contract.

The State may, at its discretion, procure necessary parts and materials separate from this Contract.

## CONTRACTOR FURNISHED MATERIALS AND TOOLS

The Contractor shall provide all tools, materials, supplies and equipment required to perform the work described in these specifications (note: this list is subject to change):

- The Contractor shall provide at no additional cost, all cleaning materials and lubricants that meet the lubricant specifications as recommended by the manufacturer;

- The State does not allow dumping or stockpiling of debris and maintenance or repair spoils on its property. The Contractor shall dispose of such waste materials in accordance with local, state and federal requirements. The Contractor shall ensure that State property is kept clean.

## RECORDS

The Contractor shall keep and maintain a log book in each machine room. The Contractor's maintenance personnel shall log in and out whenever they are in the building, and shall notify the SBM when an elevator or escalator is to be taken out of service for maintenance or repair and when an elevator or escalator is placed back in service. Additionally, when responding to an inoperable elevator or escalator call, the Contractor shall notify the SBM when the VTE is returned to service and indicate the cause of the failure and the corrective action taken to restore the elevator or escalator to service (note: this list is subject to change).

- The Contractor shall notify the SBM at the beginning and upon completion of each preventive maintenance effort, repair or retrofit activity. The Contractor shall provide the SBM with a completed preventive maintenance check chart (format shall be agreed upon between the Contractor and the SBM via a fax or email within twenty-four (24) hours of completion of the preventive maintenance procedure that adequately addresses all ASME, State, and local codes as well as items specified in this document and indicates the date, start and finish times, and total man-hours employed to complete the preventive maintenance task; wear measurements, and meter readings etc.; and any corrective actions including, adjustments, repairs, lubrication, rust/corrosion resistance (painting) activities etc.

- The Contractor shall provide and keep current a suitable check chart and repair log for each elevator and escalator, posted in the elevator and escalator machine room or other area designated by the SBM. Check charts and repair logs shall be submitted to the SBM for approval prior to use. Entries shall be made to indicate the status of all scheduled maintenance and repair work performed, including date, the nature of the work, and parts or components utilized to perform such maintenance and repairs. The check charts and repair logs shall be kept on self-duplicating data sheets and shall not be removed from their designated area by the contractor except for the purposes of reproduction. In such cases check charts and repair logs shall be returned immediately. The Contractor must properly initial the chart to indicate that the work has been accomplished. The duplicate must be clear and legible and remain in the designated area at all times. The duplicates become the property of the State.

- The Contractor shall be responsible for obtaining all technical documentation necessary for maintenance and repair of each type of VTE. The State will provide any available documentation which can be released without restriction, but it shall be the Contractor’s responsibility to make copies of such documentation. Lack of such documentation shall not be an acceptable reason for equipment downtime.

## REIMBURSABLE SERVICES

For all routine maintenance as set forth in Section 4.6, Maintenance Schedule, , price is to include full service maintenance and parts, callback service during normal working hours and all tests required by the Department of Community Affairs.

Reimbursable services may include repairs, alterations/modifications, and special projects beyond the scope of work. The Contractor shall provide written estimates to include all labor and materials for approval by the State. There shall be no additional charges for providing estimates.

The Contractor shall not provide any reimbursable services unless directed to do so by the SBM.

Hourly payment will be made for callback service at times other than during regular working hours.

## CONTRACTOR PERSONNEL

The Contractor shall ensure the following (note: this list is subject to change):

- All matters pertaining to the employment, supervision, compensation, promotion, and discharge of Contractor personnel are the responsibility of the Contractor, which is in all respects the employer of such personnel;

- All Contractor's and Subcontractor’s employees must wear uniforms approved by the SBM and bear the Contractor's name or logo;

- The Contractor shall provide photo identification badges to each employee. Contractor and Subcontractor employees shall display a photo identification badge on the outside of the outermost article of clothing at all times while the employee is on duty. Any employee reporting to work without a company identification badge shall not be permitted to enter the building;

- The SBM can require dismissal from the facilities of any employee who is identified as a potential threat to the health, safety, security, general well-being or operational mission of the facilities and occupants; and

- The Contractor shall maintain communications equipment, such as cellular phones, two-way radios, etc. The State will not provide phones, computers or internet service.

## SAFE WORK PRACTICES

All mechanics must practice safe work habits in accordance with the latest OSHA guidelines. The Contractor must comply with the following (note: this list is subject to change):

- Safety Program:

- Contractor shall establish a system wide Safety Program which will identify, eliminate, minimize, and control safety hazards and their attendant risks; and

- Contractor shall establish appropriate requirements, levels of responsibility and accountability, and method of documentation.

- The Contractor shall at all times conduct its operations in a safe manner. The Contractor shall promptly take all precautions which are reasonable or necessary to safeguard against risks, and shall make regular safety inspection of Service Equipment and Service Property;

- The Contractor shall be solely responsible for the discovery, determination and correction of any unsafe conditions arising in connection with the performance of the Contract;

- The repeated failure of any Contractor employees to follow the rules of the Safety Program or to otherwise comply with applicable safety requirements shall be the basis for removing such employee, upon the request of the SBM, from work on the Contract;

- Lockout/Tagout practice must be rigorously enforced when working on equipment, including any escalator work within the step band. Failure to follow these procedures will require the removal of any individuals not practicing safe work habits;

- Proper eye protection, footwear, hearing protection and other work clothing are the sole responsibility of the Contractor;

- The Contractor shall always place proper barricades at both ends of escalators to prevent non-authorized persons from entering the work area;

- The Contractor shall always place an Out-of-Service sign on any elevator (all landings) or escalator that is out of service for maintenance or repair;

- The Contractor shall take immediate actions to comply with all applicable laws and regulations concerning any release of a contaminant on or along State property; and

- Maintenance waste disposal shall be conducted in accordance with all local, state and federal requirements.

## ACCIDENT AND SAFETY REPORTS AND INVESTIGATIONS

- In the event of any accident involving service equipment, damage to State Property, passenger or employee accident, grade crossing accident, emergency or other non-routine event, the Contractor shall immediately notify the SBM or its authorized representative. The Contractor shall prepare all reports of such incidents as required by the State. The Contractor shall provide copies of such reports within 24 hours after the accident or other event involved. The Contractor shall comply with all applicable laws and regulations in the case of any accident;

- In the event of any accident the Contractor shall conduct an investigation to determine the cause of such accident. The investigation shall be carried out in accordance with Contractor's existing procedures; and

- The Contractor shall furnish the SBM with reports of any accident of which the Contractor has knowledge, which elevator or escalator the accident occurs on or is in any way referable to the elevators and escalators. In the event of an accident, the Contractor shall furnish a report containing statements as to the condition of the machine, repairs made at the time, and such other information as may be required by the State.

## SECURITY CLEARANCES

As a condition of employment at any State facility, the Contractor shall ensure that all personnel assigned under this Contract are subject to a New Jersey State Police Criminal History Record Background Check (Background Check). Information regarding Background Checks may be found at N.J.A.C. 13:59 and at: https://njsp.njoag.gov/criminal-history-records/.

The Contractor shall, at a minimum:

- Bear the cost of Background Checks for all assigned personnel except those assigned to the State Capitol Complex (Reference Bid Solicitation  Section 4.16.1);

- Adhere to all instructions for obtaining a Background Check as provided by the New Jersey State Police at: https://njsp.njoag.gov/criminal-history-records/;

- Ensure that any newly hired, rehired, or transferred personnel are not permitted to work in any State facility until the results of the Background Check have been furnished to the Contractor. The Contractor must review the results of the Background Check prior to assigning personnel; and

- Retain the result of each individual’s criminal history Background Check for as long as that individual is assigned to a State facility. The results of the criminal history Background Check shall be made available to the SBM upon request.

Note: If the Contractor has previously conducted a State Police background, criminal and fingerprinting check for an employee, the SBM may accept the results of said Background Check, provided that the check was performed during the Contract period or no earlier than six (6) months prior to the Contract start date. Be advised that acceptance of previously acquired Background Checks is at the sole discretion of the SBM.

In addition, the Contractor shall follow all additional Using Agency security clearance requirements, as required.

### STATE HOUSE COMPLEX-SPECIFIC BACKGROUND CHECKS & REIMBURSEMENT

The Contractor shall adhere to the procedure outlined in Bid Solicitation Attachment 7, New Jersey State House Complex Procedure for Background Checks – DPP/DPA, prior to assigning personnel at the State House Complex (Complex).

The Complex consists of the following locations:

- Executive State House – 125 West State Street, Trenton, NJ 08625;

- Legislative State House/Legislative Staff Building – 135 West State Street, Trenton, NJ 08625;

- State House Annex – 145 West State Street, Trenton, NJ 08625; and

- State House Garage – 165 West State Street, Trenton, NJ 08625;

- 225 West State Street, Trenton, NJ 08625

Note: The State House Complex Procedure for Background Checks may change during the term

of the Contract. The Contractor shall ensure that it adheres to the most up-to-date procedure for the Complex at all times.

Any Contractor personnel Background Check requested by the Division of Property Management and Construction (DPMC) and/or the Complex, for services to be provided at the Complex, will be reimbursed to the Contractor by DPMC/the Complex, as long as it is completed in accordance with the aforementioned procedure. Please note that the SBM will not accept the results of previously obtained Background Checks for workers assigned to the State House Complex unless the aforementioned procedure was followed.

Note: The Contractor will not be reimbursed for additional Background Checks required by other Using Agencies or by DPMC for any other site location.

### CRIMINAL HISTORY RECORD

The Contractor shall submit an application fingerprint card, a request for criminal history record information form (SBI-212B), and the appropriate fee for all personnel it or its Subcontractors may assign to work at any  State facility to the New Jersey State Police Bureau of Identification (SBI). The Contractor shall not permit any newly hired, re-hired, or transferred personnel to work in any facility until the SBI has furnished the results of the criminal history record background check to the Contractor. The Contractor shall review the results of that criminal history record background check prior to assigning personnel.

### CRIMINAL HISTORY RECORD FILE

The Contractor and any Subcontractor will be required to retain the results of an individual's criminal history background check as long as that person is assigned to the State  Complex under this Contract. The results of the criminal history background check shall be made available to the SBM, by the Contractor, upon request. If the Contractor or Subcontractor has had a State Police background, criminal, and fingerprinting check performed for the employee that meets the exact criteria specified above, then the check may be accepted by the SBM at the State's sole discretion. Any such reference check must have been during the Contract term  or no later than six (6) months from the Contract start date. The State reserves the right to terminate the Contract with the Contractor at any time due to breaches in security caused by the Contractor’s personnel.

## NJDOC – ADDITIONAL SECURITY REQUIREMENTS

Contractor employees providing maintenance and/or repair service to any of the New Jersey Department of Corrections (“NJDOC”) facilities will be required to go through additional security clearance.

- Maximum security facilities have the most stringent security requirements. Compliance with these requirements may require time and patience on the part of contractor’s employees, but must be followed explicitly. Failure to complete work at NJDOC facilities under this Bid Solicitation due to employee non-compliance with regard to required security measures at any correctional facility will be assessed as part of the performance review.

- All Contractors must possess a valid photo ID, i.e. State driver’s license.

The Contractor and its personnel shall be subject to and shall comply with all security regulations and procedures at each correctional facility. All contractor employees at NJDOC facilities will be subject to all security regulations and requirements at each individual correctional facility. This may include body and vehicle searches for contraband as well as prohibited items.

## PUBLIC WORKS CONTRACTOR REGISTRATION

This act specifies that no Contractor or Subcontractor shall engage in any Contract (or part thereof) for public work which is subject to the provisions of N.J.S.A 34:11-56.48, et seq. for the construction, reconstruction, demolition, alteration, custom fabrication, repair work, or maintenance work done under contract and paid for in whole or in part out of the funds of a public body or if the property or premises are owned by the public body, unless the Contractors and named Subcontractors maintain a valid public works certificate issued by the Department of Labor and Workforce Development during the duration of the Contract period.  All Contractors and named Subcontractors must maintain a valid public works certificate issued by the Department of Labor and Workforce Development in accordance with Bid Solicitation Section 3.17 and during the duration of the Contract period.

## PREVAILING WAGE

The NJ State Prevailing Wage Act, N.J.S.A. 34:11-56.25 et seq. applies to public work and building services performed under this procurement.  This Act establishes wage standards for all workers performing public work and building services for properties or premises owned or leased by the State, requiring the payment of the State Prevailing Wage rate to all employees performing those duties. See N.J.S.A. 34:11-56.25 to -56.47; N.J.S.A. 34:11-56.58 to -56.70. Prevailing wages amounts are listed by county.  It is the responsibility of the Contractor to comply with the requirements of the State Prevailing Wage Act as well as adhere to the requirements of the Fair Labor Standards Act (FLSA) during the duration of this Contract and any extensions exercised.  Prevailing wages by county can be found on the wage determinations website at https://www.nj.gov/labor/wageandhour/prevailing-rates/public-works/currentprevailingwage.shtml. If it is found that any worker employed by the Contractor or any subcontractor under the Contract has been paid a rate of wages less than the prevailing wage required to be paid under the Contract, the State may terminate the Contractor’s and/or subcontractor’s right to proceed with the work, or such part of the work as to which there has been a failure to pay required wages and may prosecute the work to completion.

## CERTIFIED PAYROLL RECORDS

N.J.A.C. 12:60-5.1 of the New Jersey Prevailing Wage Act and N.J.S.A. 34:11-56.25 et seq. requires that certified payroll records must be submitted to the public body, by all Contractors and Subcontractors, for each employee on the project within ten (10) days of the payment of wages. The Using Agency shall receive, file and make these records available for inspection during normal business hours.

## METHOD OF OPERATION

Following the award of any Contract(s) by the State as a result of this Bid Solicitation, the individual Using Agencies (including Intrastate Cooperative Purchasing Program participants) will be permitted to utilize the services under this Bid Solicitation. The awarded Contractor(s) and Using Agencies must adhere to the Method of Operation (MOO).

Using Agencies will have the option to schedule site visits and consultations with the awarded Contractor(s) for the respective Region/facility and solicit formal written Quotes for Monthly Preventative Maintenance services utilizing the hourly labor rates plus material markup percentage for that region.

Note: Monthly Preventative Maintenance services costs are not evaluated in the State’s price sheet and will be quoted per engagement

The Using Agency shall select the Contractor that is most advantageous to the State and meets the needs of the Using Agency, price and other factors considered. The Using Agency shall notify all Contractors of the selected Contractor for Monthly Preventative Maintenance. The preventative maintenance costs shall be All-Inclusive of the services provided in various sections in Section 4.0, Scope of Work and should include the awarded pricing for the hourly labor rates plus material markup percentage of the specific Contractor for that region. Using Agencies will have the option to contact another awarded Contractor to repair or service equipment if the Contractor is unable to repair equipment for any reason or make necessary repairs within a week of the initial request.

Any work that falls outside of the monthly maintenance service agreement should utilize the Price Lines awarded to the Contractor.

Using Agencies can submit a request to DPP to add or modify facilities, locations, and contacts to the Bid Solicitation Attachment #6, State Location List.

## GEOGRAPHICAL REGIONS

Contractors shall provide services in all counties of its awarded region(s). This Contract shall be divided and awarded into four (4) separate regions as follows: North, Central,  South, and Capitol Complex. Counties comprising each region are indicated below:

| Region 1 - North | Region 2 - Central | Region 3 - South | Region 4 – Capitol Complex |
| --- | --- | --- | --- |
| Bergen County | Hunterdon County | Atlantic County | See Attachment #6 – State Location List |
| Essex County | Mercer County | Burlington County |  |
| Hudson County | Middlesex County | Camden County |  |
| Morris County | Monmouth County | Cape May County |  |
| Passaic County | Somerset County | Cumberland County |  |
| Sussex County |  | Gloucester County |  |
| Union County |  | Ocean County |  |
| Warren County |  | Salem County |  |

# GENERAL CONTRACT TERMS

The Contractor shall have sole responsibility for the complete effort specified in this Contract.  Payment will be made only to the Contractor or to the authorized dealers/distributors, if applicable.  The Contractor is responsible for the professional quality, technical accuracy and timely completion and submission of all deliverables, services or commodities required to be provided under this Contract.  The Contractor shall, without additional compensation, correct or revise any errors, omissions, or other deficiencies in its deliverables and other services.  The approval of deliverables furnished under this Contract shall not in any way relieve the Contractor of responsibility for the technical adequacy of its work.  The review, approval, Acceptance or payment for any of the deliverables, goods or services, shall not be construed as a waiver of any rights that the State may have arising out of the Contractor’s performance of this Contract.

## CONTRACT TERM AND EXTENSION OPTION

The base term of this Contract shall be for a period of three (3) years.  The anticipated Contract effective date is provided on the “Summary” page of the Bid Solicitation in NJSTART.  If delays in the procurement process result in a change to the anticipated Contract effective date, the Contractor agrees to accept a Contract for the full term of this Contract.

This Contract may be extended up to three (3) years with no single extension exceeding one (1) year, by the mutual written consent of the Contractor and the Director at the same terms, conditions, and pricing at the rates in effect in the last year of this Contract or rates more favorable to the State.

## CONTRACT TRANSITION

No Award Made --In the event that a new contract has not been awarded prior to the expiration date for this Contract, including any extensions exercised, then by written notice to the Contractor, the State may exercise its right to transition this Contract for a period of up to 180 Calendar Days (the “Initial Transition Period”).  In the event the State exercises its right pursuant to this Section, then the Contractor shall continue performance under this Contract under the same terms, conditions, and pricing until a new contract is awarded or the Initial Transition Period expires. At no time shall this Initial Transition Period extend more than 365 Calendar Days beyond the expiration date of this Contract, including any extensions exercised, unless in the opinion of the Director, it is in the best interest of the State to extend the Initial Transition Period.

New Contract Awarded -- In the event that a new contract has been awarded prior to the expiration date for this Contract, including any extensions exercised , then by written notice to the Contractor the State may transition this Contract (the “NCA Transition Period”) and the Contractor shall continue performance under this Contract, under the same terms, conditions, and pricing, for a period of up to 365 Calendar Days beyond the expiration date of this Contract, including any extensions exercised, or until the new contract(s) can be completely operational, whichever first occurs.

## PERFORMANCE SECURITY

Not applicable to this procurement.

## OWNERSHIP OF MATERIAL

- State Data – The State owns State Data. Contractor shall not obtain any right, title, or interest in any State Data, or information derived from or based on State Data.  State Data provided to Contractor shall be delivered or returned to the State of New Jersey upon thirty (30) days’ notice by the State or thirty (30) days after the expiration or termination of the Contract.  Except as specifically required by the requirements of the Bid Solicitation, State Data shall not be disclosed, sold, assigned, leased or otherwise disposed of to any person or entity other than the State unless specifically directed to do so in writing by the State Contract Manager.

Work Product; Services – The State owns all Deliverables developed for the State in the course of providing Services under the Contract, including but not limited to, all data, technical information, materials gathered, originated, developed, prepared, used or obtained in the performance of the Contract, including but not limited to all reports, surveys, plans, charts, literature, brochures, mailings, recordings (video and/or audio), pictures, drawings, analyses, graphic representations, print-outs, notes and memoranda, written procedures and documents, regardless of the state of completion, which are prepared for or are a result of the Services required under the Contract.

Contractor Intellectual Property; Commercial off the Shelf Software (COTS) and Customized Software – Contractor retains ownership of all Contractor Intellectual Property, and any modifications thereto and derivatives thereof, that the  Contractor supplies to the State pursuant to the Contract, and grants the State a non-exclusive, royalty-free license to use Contractor Intellectual Property delivered to the State for the purposes contemplated by the Contract for the duration of the Contract including all extensions.  In the event Contractor provides its standard license agreement terms with its Quote, such terms and conditions must comply with Bid Solicitation Section 1.4 – Order of Precedence of Contractual Terms.

Third Party Intellectual Property – Unless otherwise specified in the Bid Solicitation that the State, on its own, will acquire and obtain a license to Third Party Intellectual Property, Contractor shall secure on the State’s behalf, in the name of the State and subject to the State’s approval, a license to Third Party Intellectual Property sufficient to fulfill the business objectives, requirements and specifications identified in the Contract at no additional cost to the State beyond that in the Quote price.  In the event Contractor is obligated to flow-down commercially standard third party terms and conditions customarily provided to the public associated with Third Party Intellectual Property and such terms and conditions conflict with Bid Solicitation requirements, including the SSTC, the State will accept such terms and conditions with the exception of the following:  indemnification, limitation of liability, choice of law, governing law, jurisdiction, and confidentiality.  The Bid Solicitation including the SSTC shall prevail with respect to such conflicting terms and conditions.  In addition, the State will not accept any provision requiring the State to indemnify a third party or to submit to arbitration.  Such terms are considered void and of no effect.  Third party terms and conditions should be submitted with the Quote. If Contractor uses Third Party Intellectual Property, Contractor must indemnify the State for infringement claims with respect to the Third Party Intellectual Property.   Contractor agrees that its use of Third Party Intellectual Property shall be consistent with the license for the Third Party Intellectual Property, whether supplied by the Contractor, secured by the State as required by the Bid Solicitation, or otherwise supplied by the State.

Work Product; Custom Software – The State owns all Custom Software which shall be considered “work made for hire”, i.e., the State, not the Contractor, Subcontractor, or third party, shall have full and complete ownership of all such Custom Software.  To the extent that any Custom Software may not, by operation of the law, be a “work made for hire” in accordance with the terms of the Contract, Contractor, Subcontractor, or third party hereby assigns to the State, or Contractor shall cause to be assigned to the State, all right, title and interest in and to any such Custom Software and any copyright thereof, and the State shall have the right to obtain and hold in its own name any copyrights, registrations and any other proprietary rights that may be available.

State Intellectual Property – The State owns all State Intellectual Property provided to Contractor pursuant to the Contract.  State Intellectual Property shall be delivered or returned to the State of New Jersey upon thirty (30) days’ notice by the State or thirty (30) days after the expiration or termination of the Contract.  The State grants Contractor a non-exclusive, royalty-free, license to use State Intellectual Property for the purposes contemplated by the Contract.  Except as specifically required by the requirements of the Bid Solicitation, State Intellectual Property shall not  be disclosed, sold, assigned, leased or otherwise disposed of to any person or entity other than the State unless specifically directed to do so in writing by the State Contract Manager. The State’s license to Contractor is limited by the term of the Contract and the confidentiality obligations set forth in Bid Solicitation Section 6 – Data Security Requirements – Contractor Responsibility.

No Rights – Except as expressly set forth in the Contract, nothing in the Contract shall be construed as granting to or conferring upon Contractor any right, title, or interest in State Intellectual Property or any intellectual property that is now owned or licensed to or subsequently owned by or licensed by the State.  Except as expressly set forth in the Contract, nothing in the Contract shall be construed as granting to or conferring upon the State any right, title, or interest in any Contractor Intellectual Property that is now owned or subsequently owned by Contractor.  Except as expressly set forth in the Contract, nothing in the Contract shall be construed as granting to or conferring upon the State any right, title, or interest in any Third Party Intellectual Property that is now owned or subsequently owned by a third party.

## SUBSTITUTION OF STAFF

If a Contractor needs to substitute any management, supervisory or key personnel, the Contractor shall identify the substitute personnel and the work to be performed.  The Contractor must provide detailed justification documenting the necessity for the substitution.  Resumes must be submitted for the individual(s) proposed as substitute(s) who must have qualifications and experience equal to or better than the individual(s) originally proposed or currently assigned.

The Contractor shall forward a request to substitute staff to the State Contract Manager for consideration and approval.  No substitute personnel are authorized to begin work until the Contractor has received written approval to proceed from the State Contract Manager.

## DELIVERY TIME AND COSTS

Not applicable to this procurement.

## AUTHORIZED DEALER AND/OR DISTRIBUTORS

Not applicable to this procurement.

## LIQUIDATED DAMAGES

Not applicable to this procurement.

## RETAINAGE

Not applicable to this procurement.

## ELECTRONIC PAYMENTS

With the award of this Contract, the successful Contractor(s) will be required to receive its payment(s) electronically.  In order to receive payments via automatic deposit from the State of New Jersey, the Contractor must complete the EFT information within its NJSTART Vendor Profile.  Please refer to the QRG entitled “Vendor Profile Management – Company Information and User Access” for instructions.

## PROCUREMENT EFFICIENCY PROGRAM

- Quarterly Sales Reporting - The Contractor shall submit a Sales Report documenting all sales made under the Contract.  The Sales Report shall be submitted directly to Periscope no later than thirty (30) Calendar Days after the end of each calendar quarter. The calendar quarters will end March 31, June 30, September 30, and December 31. The Sales Report must contain the following information:

  - Complete and accurate details of all sales, credits, returns, refunds, and the like for the reporting quarter;

  - Purchasing entity;

  - Total of Procurement Efficiency Program Fee amount due for the reporting quarter;

  - Such other information as the State may reasonably request;

  - If no sales were made against this Contract during the reporting quarter, then a report shall be submitted showing zero sales and zero Procurement Efficiency Program Fee due; and

  - Quarterly Sales Reporting and remittance of the Procurement Efficiency Program Fee shall begin on the first calendar quarter starting after the effective date of the Contract.

- Procurement Efficiency Program Fee - For all purchases made under this Contract, that have been invoiced, the Contractor shall remit the Procurement Efficiency Program Fee in the amount of one percent (1%) of all Purchases to Periscope acting on behalf of the State of New Jersey.

- Remittance of the Procurement Efficiency Program Fee - On a quarterly basis, the Contractor shall remit the Procurement Efficiency Program Fee directly to Periscope no later than thirty (30) days after the end of each calendar quarter. The calendar quarters will end March 31, June 30, September 30, and December 31.  Failure to remit the Procurement Efficiency Program Fee timely and accurately may result in Contract termination as outlined in the “Termination of Contract” clause of the State of New Jersey Standard Terms and Conditions.

- NJSTART Marketplace Catalog Enablement - Contractor shall cooperate with State and/or Periscope as requested to upload catalog items and pricing consistent with this Contract. Contractor shall upload catalog within thirty (30) Calendar Days of the date of execution of this Contract. Failure to cooperate will result in the Contractor’s good and/or services not being represented in the NJSTART Marketplace. The Contractor shall ensure that the catalog complies with the scope, and terms and conditions of this Contract. Any identified deviation from the Contract must be corrected immediately. Any catalog that does not comply with the scope and terms and conditions of this Contract can lead to a breach of contract and will be escalated to the Division of Purchase and Property’s Contract Compliance and Audit Unit for review and possible action.

- Retention and Inspection of Records and Audit - The Contractor shall keep records of all sales made to all Using Agencies in sufficient detail to enable the State to determine the Procurement Efficiency Program Fee payable by the Contractor. The State and/or Periscope may examine and audit, at its own expense, Contractor’s sales records and Sales Reports for completeness and accuracy. If such examination reveals underpayment of the Procurement Efficiency Program Fee, the Contractor shall immediately pay to Periscope the amount of deficiency. If the examination reveals an underpayment of 5% or more, then the Contractor shall reimburse the State and/or Periscope for the cost of the audit.

# DATA SECURITY REQUIREMENTS – CONTRACTOR RESPONSIBILITY

Not applicable to this procurement.

# MODIFICATIONS TO THE STATE OF NEW JERSEY STANDARD TERMS AND CONDITIONS

## INSURANCE

### PROFESSIONAL LIABILITY INSURANCE

Section 4.2 of the SSTC regarding insurance is modified with the addition of the following section regarding Professional Liability Insurance.

Professional Liability Insurance:  The Contractor shall carry Errors and Omissions, Professional Liability Insurance, and/or Professional Liability Malpractice Insurance sufficient to protect the Contractor from any liability arising out the professional obligations performed pursuant to the requirements of this Contract.  The insurance shall be in the amount of not less than $1,000,000 if appropriate and in such policy forms as shall be approved by the State.  If the Contractor has claims-made coverage and subsequently changes carriers during the term of this Contract, it shall obtain from its new Errors and Omissions, Professional Liability Insurance, and/or Professional Malpractice Insurance carrier an endorsement for retroactive coverage.

# QUOTE EVALUATION AND AWARD

## RIGHT TO WAIVE

Pursuant to N.J.A.C. 17:12-2.7(d) the Director may waive minor irregularities or omissions in a Quote.  The Director reserves the right to waive a requirement provided that the requirement does not materially affect the procurement or the State's interests associated with the procurement.

## DIRECTOR’S RIGHT TO ACCEPT OR REJECT A QUOTE

The Director reserves the right to reject any or all Quotes, or to award in whole or in part if deemed to be in the best interest of the State to do so. The Director shall have authority to award Contracts in accordance with N.J.S.A. 52:34-12.

## RECIPROCITY FOR JURISDICTIONAL BIDDER PREFERENCE

In accordance with N.J.S.A. 52:32-1.4 and N.J.A.C. 17:12-2.13, the State of New Jersey will invoke reciprocal action against an out-of-State Bidder whose state or locality maintains a preference practice for its in-state Bidders.  The State of New Jersey will use the annual surveys compiled by the Council of State Governments, National Association of State Procurement Officials, or the National Institute of Governmental Purchasing or a State’s statutes and regulations to identify States having preference laws, regulations, or practices and to invoke reciprocal actions. The State of New Jersey may obtain additional information as it deems appropriate to supplement the stated survey information.

A Bidder may submit information related to preference practices enacted for a State or Local entity outside the State of New Jersey. This information may be submitted in writing as part of the Quote response, including name of the locality having the preference practice, as well as identification of the county and state, and should include a copy of the appropriate documentation, i.e., resolution, regulation, law, notice to Bidder, etc.  It is the responsibility of the Bidder to provide documentation with the Quote or submit it to the Director within five (5) Business Days after the deadline for Quote submission.  Written evidence for a specific procurement that is not provided to the Director within five (5) Business Days of the public Quote submission date may not be considered in the evaluation of that procurement, but may be retained and considered in the evaluation of subsequent procurements.

## CLARIFICATION OF QUOTE

After the Quote Opening Date, unless requested by the State as noted below, Bidder contact with the Procurement Bureau regarding this Bid Solicitation and the submitted Quote is not permitted.

After the Quotes are reviewed, one (1), some or all of the Bidders may be asked to clarify certain aspects of its Quote.  A request for clarification may be made in order to resolve minor ambiguities, irregularities, informalities or clerical errors.  Clarifications cannot correct any deficiencies, material omissions, or used to revise or modify a Quote.

The Director reserves the right to request that a Bidder explain, in detail, how the Quote price was determined.

## ORAL PRESENTATION

Not applicable to this procurement.

## TIE QUOTES

Tie Quotes will be awarded by the Director in accordance with N.J.A.C. 17:12-2.10.

## STATE'S RIGHT TO INSPECT BIDDER’S FACILITIES

The State reserves the right to inspect the Bidder’s establishment before making an award, for the purposes of ascertaining whether the Bidder has the necessary facilities for performing the Contract.

## STATE'S RIGHT TO CHECK REFERENCES

The State may also consult with clients of the Bidder during the evaluation of Quotes. Such consultation is intended to assist the State in making a Contract award that is most advantageous to the State.

## EVALUATION CRITERIA

The following evaluation criteria categories, not necessarily listed in order of significance, will be used to evaluate Quotes received in response to this Bid Solicitation.  The evaluation criteria categories may be used to develop more detailed evaluation criteria to be used in the evaluation process.

### TECHNICAL EVALUATION CRITERIA

The following criteria will be used to evaluate and score Quotes received in response to this Bid Solicitation:

- The Bidder’s demonstration in the Quote that the Bidder understands and is able to complete the requirements of the Scope of Work as sought.

### PRICE EVALUATION

For evaluation purposes, Bidders will be ranked from lowest to highest according to the total Quote price located on the State-Supplied Price Sheet accompanying this Bid Solicitation. The Mark-Up percentage will be excluded from the total Quote price. Additionally, all submitted prices will be evaluated for reasonableness.

## QUOTE DISCREPANCIES

In evaluating Quotes, discrepancies between words and figures will be resolved in favor of words.  Discrepancies between Unit Prices and totals of Unit Prices will be resolved in favor of Unit Prices.  Discrepancies in the multiplication of units of work and Unit Prices will be resolved in favor of the Unit Prices.  Discrepancies between the indicated total of multiplied Unit Prices and units of work and the actual total will be resolved in favor of the actual total.  Discrepancies between the indicated sum of any column of figures and the correct sum thereof will be resolved in favor of the correct sum of the column of figures.

## NEGOTIATION

In accordance with N.J.S.A. 52:34-12(f) and N.J.A.C. 17:12-2.7, after evaluating Quotes, the Procurement Bureau may establish a competitive range and enter into negotiations with one (1) Bidder or multiple Bidders within this competitive range.  The primary purpose of negotiations is to maximize the State’s ability to obtain the best value based on the mandatory requirements, evaluation criteria, and cost.  Multiple rounds of negotiations may be conducted with one (1) Bidder or multiple Bidders.  Negotiations will be structured by the Procurement Bureau to safeguard information and ensure that all Bidders are treated fairly.

Negotiations will be conducted only in those circumstances where it is deemed by the Director to be in the State’s best interests and to maximize the State’s ability to get the best value.  Therefore, the Bidder is advised to submit its best technical and price Quote in response to this Bid Solicitation since the State may, after evaluation, make a Contract award based on the content of the initial submission.

If the Procurement Bureau contemplates negotiation, Quote prices will not be publicly read at the Quote opening.  Only the name and address of each Bidder will be publicly announced at the Quote opening.

## BEST AND FINAL OFFER (BAFO)

The Bidder is advised to submit its most competitive technical and price Quote in response to this Bid Solicitation. The State reserves the right to award a Contract based on the initial pricing submitted without requesting a Best and Final Offer (BAFO).  BAFOs will be conducted only in those circumstances where it is deemed by the Director to be in the State’s best interests and to maximize the State’s ability to get the best value.

The Procurement Bureau may invite one (1) Bidder or multiple Bidders to submit a BAFO. Said invitation will establish the time and place for submission of the BAFO.  The Division may conduct more than one (1) round of BAFO in order to attain the best value for the State. Any BAFO that does not result in more advantageous pricing to the State will not be considered, and the State will evaluate the Bidder’s most advantageous previously submitted pricing.

If the Procurement Bureau contemplates BAFOs, Quote prices will not be publicly read at the Quote opening.  Only the name and address of each Bidder will be publicly announced at the Quote opening.

## “REQUEST FOR REVISION” WITHIN NJSTART

The State may request a revision of the Bidder’s Quote within NJSTART. The Bidder shall respond to the “Request for Revision” only for the reason(s) identified by the State. Any changes made by a Bidder to the Quote other than as requested by the State shall be considered null and void.

## POOR PERFORMANCE

A Bidder with a history of performance problems may be bypassed for consideration of an award issued as a result of this Bid Solicitation. The following materials may be reviewed to determine Bidder performance:

- Contract cancellations for cause pursuant to State of New Jersey Standard Terms and Conditions Section 5.7(B);

- Information contained in Contractor performance records;

- Information obtained from audits or investigations conducted by a local, state or federal agency of the Bidder’s work experience;

- Current licensure, registration, and/or certification status and relevant history thereof; or

- Bidder’s status or rating with established business/financial reporting services, as applicable.

Bidders should note that this list is not exhaustive.

## RECOMMENDATION FOR AWARD

After the evaluation of the submitted Quotes is complete, the Procurement Bureau will recommend to the Director for award, the responsible Bidder(s) whose Quote, conforming to this Bid Solicitation, is most advantageous to the State, price and other factors considered.  The Director may accept, reject or modify the recommendation of the Procurement Bureau.

## CONTRACT AWARD

Contract award(s) will be made with reasonable promptness by written notice to those responsible Bidder(s), whose Quote(s), conforming to this Bid Solicitation, are most advantageous to the State, price, and other factors considered.  Any or all Quotes may be rejected when the State Treasurer or the Director determines that it is in the public interest to do so.  Contract awards will be publicly posted under the relevant contract number and available on NJSTART.

For the purposes of pricing for this Contract, the State of New Jersey has been divided into four (4) regions, with each region being evaluated and awarded separately. Each Region contains thirteen (13) price lines. The first twelve (12) price lines of each grouping (1-12, 14-25, 27-38, and 40-51) must be bid upon in order to be deemed responsive for the given Region.

This Bid Solicitation has been designated as a partial Small Business set-aside Contract for Small Business Category I, II or III, as per Section 3.8. The State intends to award to at least one (1) bidder, and up to six (6), per region, with one (1) award per region set-aside for qualifying Small Businesses.

# GLOSSARY

## CROSSWALK

| Current DPP Template Term | Equivalent Statutory, Regulatory NJSTART and/or Legacy Term |
| --- | --- |
| Bid Solicitation | Request For Proposal (RFP)/Solicitation |
| Bid Amendment | Addendum |
| Contract | Master Blanket Purchase Order (Blanket/Blanket P.O.) |
| Contract Amendment | Change Order |
| Administrative Change Order | Change Order |
| Quote | Proposal/Bid |
| Contractor | Vendor/Contractor |
| Bidder | Bidder/Contractor |

## DEFINITIONS

Unless otherwise specified in the Bid Solicitation, the following definitions will be part of any Contract awarded, or order placed, as a result of this Bid Solicitation.  Note that not all definitions included here apply to all Bid Solicitations.

Acceptance – The written confirmation by the Using Agency that Contractor has completed a Deliverable according to the specified requirements.

Administrative Change Order – A unilateral administrative modification to the Contract in the NJSTART system by the Division. Administrative Change Orders are not to be considered formal Contract Amendments.

All-Inclusive Hourly Rate – An hourly rate comprised of all direct and indirect costs including, but not limited to: labor costs, overhead, fee or profit, clerical support, travel expenses, per diem, safety equipment, materials, supplies, managerial support and all documents, forms, and reproductions thereof.  This rate also includes portal-to-portal expenses as well as per diem expenses such as food.

Apparel – means any clothing, headwear, linens or fabric.

Apparel Contracts – include all purchases, rentals or other acquisition of apparel products by the State of New Jersey, including authorizations by the State of New Jersey for contractors to sell apparel products through cash allowances or vouchers issued by the State of New Jersey, and license agreements with a public body.

Apparel Production – includes the cutting and manufacturing of apparel products performed by the contractor or by any Subcontractors, but not including the production of supplies or sundries such as buttons, zippers, and thread.

Approved Products – Those products that have been identified in Bid Solicitation as meeting Using Agency needs and confirmed as meeting product specifications.

Authorized Purchasers – shall mean any State-Level government agency, department, office, instrumentality, division, unit or other entity in the Executive Branch (“State Purchasers”), Cooperative Purchasing Partners, and/or Intrastate Cooperative Purchasing Partners.

Best and Final Offer or BAFO – Pricing timely submitted by a Bidder upon invitation by the Procurement Bureau after Quote opening, with or without prior discussion or negotiation.

Bid or Bid Solicitation – The documents which establish the bidding and Contract requirements and solicits Quotes to meet the needs of the Using Agencies as identified herein, and includes the Bid Solicitation, State of New Jersey Standard Terms and Conditions (SSTC), State-Supplied Price Sheet, Attachments, and Bid Amendments.

Bid Amendment – Written clarification or revision to this Bid Solicitation issued by the Division. Bid Amendments, if any, will be issued prior to Quote opening.

Bid Opening Date – The date Quotes will be opened for evaluation and closed to further Quote submissions.

Bid Security - means a guarantee, in a form acceptable to the Division, that the bidder, if selected, will accept the contract as bid; otherwise, the bidder or, as applicable, its guarantor will be liable for the amount of the loss suffered by the State, which loss may be partially or completely recovered by the State in exercising its rights against the instrument of bid security.

Bidder – An entity offering a Quote in response to the Division’s Bid Solicitation.

Breach of Security – as defined by N.J.S.A. 56:8-161, means unauthorized access to electronic files, media, or data containing Personal Data that compromises the security, confidentiality, or integrity of Personal Data when access to the Personal Data has not been secured by encryption or by any other method or technology that renders the Personal Data unreadable or unusable.  Good faith acquisition of Personal Data by an employee or agent of the Provider for a legitimate business purpose is not a Breach of Security, provided that the Personal Data is not used for a purposes unrelated to the business or subject to further unauthorized disclosure.

Business Day – Any weekday, excluding Saturdays, Sundays, State legal holidays, and State-mandated closings unless otherwise indicated.

Calendar Day – Any day, including Saturdays, Sundays, State legal holidays, and State-mandated closings unless otherwise indicated.

Commercial off the Shelf Software or COTS – Software provided by Provider that is commercially available and that can be used with little or no modification.

Contract – The Contract consists of the State of NJ Standard Terms and Conditions (SSTC), the Bid Solicitation, the responsive Quote submitted by a responsible Bidder as accepted by the State, the notice of award, any Best and Final Offer, any subsequent written document memorializing the agreement, any modifications to any of these documents approved by the State and any attachments, Bid Amendment or other supporting documents, or post-award documents including Contract Amendments agreed to by the State and the Contractor, in writing.

Contract Amendment – An amendment, alteration, or modification of the terms of a Contract between the State and the Contractor(s). A Contract Amendment is not effective until it is signed and approved in writing by the person with the appropriate signing authority.  Contract Amendments are tracked using Change Orders in NJSTART. Please note that Administrative Change Orders (see definition above) are not considered Contract Amendments.

Contractor – The Bidder awarded a Contract resulting from this Bid Solicitation.

Contractor Intellectual Property – Any intellectual property that is owned by Contractor and contained in or necessary for the use of the Deliverables or which the Contractor makes available for the State to use as part of the work under the Contract.  Contractor Intellectual Property includes COTS or Customized Software owned by Contractor, Contractor’s technical documentation, and derivative works and compilations of any Contractor Intellectual Property.

Cooperative Purchasing Program – The Division’s intrastate program that provides procurement-related assistance to New Jersey local governmental entities and boards of education, State and county colleges and other public entities having statutory authority to utilize select State Contract s issued by the Division, pursuant to the provisions of N.J.S.A. 52:25-16.1 et seq.

Cooperative Purchasing Participants – These participants include quasi-State entities, counties, municipalities, school districts, volunteer fire departments, first aid squads, independent institutions of higher learning, County colleges, and State colleges.

Customized Software – COTS that is adapted or configured by Provider to meet specific requirements of the Authorized Purchaser that differ from the standard requirements of the base product. For the avoidance of doubt, “Customized Software” is not permitted to be sold to the State under the scope of this Contract.

Days After Receipt of Order (ARO) – The number of Calendar Days ‘After Receipt of Order’ in which the Using Agency will receive the ordered materials and/or services.

Dealer/Distributor – A Company authorized by a Bidder or Contractor as having the contractual ability to accept and fulfill orders and receive payments directly on behalf of the Contractor that is awarded a Contract.  Any authorized Dealer/Distributor must agree to all terms and conditions contained within the Bid Solicitation and must agree to provide all products and services in accordance with the Contract specifications, terms, conditions and pricing.

Deliverable – Goods, products, Services and Work Product that Contractor is required to deliver to the State under the Contract.

Director – Director, Division of Purchase and Property, Department of the Treasury, who by statutory authority is the Chief Contracting Officer for the State of New Jersey; or the Director’s designee.

Disabled Veterans’ Business - means a business which has its principal place of business in the State, is independently owned and operated and at least 51% of which is owned and controlled by persons who are disabled veterans or a business which has its principal place of business in this State and has been officially verified by the United States Department of Veterans Affairs as a service disabled veteran-owned business for the purposes of department contracts pursuant to federal law.  N.J.S.A. 52:32-31.2.

Disabled Veterans’ Business Set-Aside Contract – means a Contract for goods, equipment, construction or services which is designated as a Contract with respect to which bids are invited and accepted only from disabled veterans’ businesses, or a portion of a Contract when that portion has been so designated.  N.J.S.A. 52:32-31.2.

Discount – The standard price reduction applied by the Bidder to all items.

Division – The Division of Purchase and Property.

Equivalent Products – Products offered other than those identified as an Approved Product in this Bid Solicitation that meet the specifications herein. Equivalent Products will be evaluated to ensure that they meet all technical, nutritional, and packaging specifications herein as part of the Quote evaluation process.

Evaluation Committee – A group of individuals or a Division staff member assigned by the Director to review and evaluate Quotes submitted in response to this Bid Solicitation and recommend a Contract award to the Director.

Firm Fixed Price – A price that is all-inclusive of direct cost and indirect costs, including, but not limited to, direct labor costs, overhead, fee or profit, clerical support, equipment, materials, supplies, managerial (administrative) support, all documents, reports, forms, travel, reproduction and any other costs.

Hardware – Includes computer equipment and any Software provided with the Hardware that is necessary for the Hardware to operate.

Internet of Things (IoT) – the network of physical devices, vehicles, home appliances and other items embedded with electronics, software, sensors, actuators, and network connectivity which enables these objects to connect and exchange data.

Intrastate cooperative purchasing participants – refers to political subdivisions, volunteer fire departments and first aid squads, and independent institutions of higher education and school districts pursuant to N.J.S.A. 52:25-16.1 et seq., State and county colleges pursuant to N.J.S.A. 18A:64-60 and 18A:64A-25.9, quasi-State agencies and independent authorities pursuant to N.J.S.A. 52:27B-56.1, and other New Jersey public entities having statutory authority to utilize select State contracts issued by the Division.

Joint Venture – A business undertaking by two (2) or more entities to share risk and responsibility for a specific project.

Life cycle assessment – The comprehensive examination of a product’s environmental and economic aspects and potential impacts throughout its lifetime, including raw material extraction, transportation, manufacturing, use and disposal.

Life cycle cost – The amortized total cost of a product, including capital costs, installation costs, operating costs, maintenance costs, and disposal costs discounted over the lifetime of the product.

Master Blanket Purchase Order (Blanket/Blanket P.O.) – A Term Contract that allows repeated purchases from an awarded contract.

Materials in Solid Waste – Material found in the various components of the solid waste stream. General, solid waste has several components, such as municipal solid waste (MSW), construction and demolition debris (C&D), and nonhazardous industrial waste.  Under RCRA Section 6002, EPA considers materials recovered from any component of the solid waste stream when designating items containing Recovered Materials.

May – Denotes that which is permissible or recommended, not mandatory.

Mobile Device – means any device used by Provider that can move or transmit data, including but not limited to laptops, hard drives, and flash drives.

Must – Denotes that which is a mandatory requirement.

Net Purchases – means the total gross purchases, less credits, taxes, regulatory fees and separately stated shipping charges not included in unit prices, made by Intrastate Cooperative Purchasing Participants, regardless of whether or not NJSTART is used as part of the purchase process.

No Bid – The Bidder is not submitting a price Quote for an item on a price line.

No Charge – The Bidder will supply an item on a price line free of charge.

Non-Public Data – means data, other than Personal Data, that is not subject to distribution to the public as public information. Non-Public Data is data that is identified by the State as non-public information or otherwise deemed to be sensitive and confidential by the State because it contains information that is exempt by statute, ordinance or administrative rule from access by the general public as public information.

Percentage Discount or Markup – The percentage bid applied as a Markup or a Discount to a firm, fixed price contained within a price list/catalog.

Performance Security – means a guarantee, executed subsequent to award, in a form acceptable to the Division, that the successful bidder will complete the contract as agreed and that the State will be protected from loss in the event the contractor fails to complete the contract as agreed.

Personal Data means –

“Personal Information” as defined in N.J.S.A. 56:8-161, means an individual’s first name or first initial and last name linked with any one or more of the following data elements: (1) Social Security number, (2) driver’s license number or State identification card number or (3) account number or credit or debit card number, in combination with any required security code, access code, or password that would permit access to an individual’s financial account.  Dissociated data that, if linked would constitute Personal Information is Personal Information if the means to link the dissociated were accessed in connection with access to the dissociated data.  Personal Information shall not include publicly available information that is lawfully made available to the general public from federal, state or local government records, or widely distributed media; and/or

Data, either alone or in combination with other data, that includes information relating to an individual that identifies the person or entity by name, identifying number, mark or description that can be readily associated with a particular individual and which is not a public record, including but not limited to, Personally Identifiable Information (PII); government-issued identification numbers (e.g., Social Security, driver’s license, passport); Protected Health Information (PHI) as that term is defined in the regulations adopted pursuant to the Health Insurance Portability and Accountability Act of 1996, P.L. No. 104-191 (1996) and found in 45 CFR Parts 160 to 164 and defined below; and Education Records, as that term is defined in the Family Educational Rights and Privacy Act (FERPA), 20 U.S.C. § 1232g.

Personally Identifiable Information or PII - as defined by the U.S. Department of Commerce, National Institute of Standards and Technology, means any information about an individual maintained by an agency, including (1) any information that can be used to distinguish or trace an individual’s identity, such as name, social security number, date and place of birth, mother’s maiden name, or biometric records; and (2) any other information that is linked or linkable to an individual, such as medical, educational, financial, and employment information.

Post-Consumer Material – Material or finished product that has served its intended use and has been diverted or recovered from waste destined for disposal, having completed its life as a consumer item.  Post-Consumer Materials are part of the broader category of Recovered Materials.

Pre-Consumer Material – Materials generated in manufacturing and converting processes, such as manufacturing scrap and trimmings/cuttings.

Price List/Catalog – A document published by a manufacturer, resellers, Dealers, or Distributors that typically contains product descriptions, a list of products with fixed prices to which a Bidder’s percentage discount or markup bid is applied.

Procurement Bureau (Bureau) – The Division unit responsible for the preparation, advertisement, and issuance of Bid Solicitations, for the tabulation of Quotes and for recommending award(s) of Contract(s) to the Director and the Deputy Director.

Project – The undertakings or services that are the subject of this Bid Solicitation.

Protected Health Information or PHI – has the same meaning as the term is defined in the regulations adopted pursuant to the Health Insurance Portability and Accountability Act of 1996, P.L. No. 104-191 (1996) and found in 45 CFR Parts 160 to 164 means Individually Identifiable Health Information (as defined below) transmitted by electronic media, maintained in electronic media, or transmitted or maintained in any other form or medium. PHI excludes education records covered by the Family Educational Rights and Privacy Act (FERPA), as amended, 20 U.S.C. 1232g, records described at 20 U.S.C. 1232g(a)(4)(B)(iv) and employment records held by a covered entity in its role as employer. The term “Individually Identifiable Health Information” has the same meaning as the term is defined in the regulations adopted pursuant to the Health Insurance Portability and Accountability Act of 1996, P.L. No. 104-191 (1996) and found in 45 CFR Parts 160 to 164 and means information that is a subset of Protected Health Information, including demographic information collected from an individual, and (1) is created or received by a health care provider, health plan, employer or health care clearinghouse; and (2) relates to the past, present or future physical or mental health or condition of an individual; the provision of health care to an individual; or the past, present or future payment for the provision of health care to an individual; and (a) that identifies the individual; or (b) with respect to which there is a reasonable basis to believe the information can be used to identify the individual.

Purchases - means the total gross purchases, less credits, taxes, regulatory fees and separately stated shipping charges not included in unit prices, made regardless of whether or not NJSTART is used as part of the purchase process.

Quasi-State Agency – is any agency, commission, board, authority or other such governmental entity which is established and is allocated to a State department or any bi-state governmental entity of which the State of New Jersey is a member, as defined in N.J.S.A. 52:27B-56.1, provided that any sale to any such bi-state governmental entity is for use solely within the State of New Jersey.

Quick Reference Guides (QRGs) – Informational documents which provide Vendors with step-by-step instructions to navigate the NJSTART eProcurement System. QRGs are available on the NJSTART Vendor Support Page.

Quote – Bidder’s timely response to the Bid Solicitation including, but not limited to, technical Quote, price Quote including Best and Final Offer, any licenses, forms, certifications, clarifications, negotiated documents, and/or other documentation required by the Bid Solicitation.

Quote Opening Date – The date Quotes will be opened for evaluation and closed to further Quote submissions.

Recovered Material – Waste material and byproduct that have been recovered or diverted from solid waste, but does not include materials and byproducts generated from, and commonly reused within, an original manufacturing process.

Recycling – The series of activities, including collection, separation, and processing, by which products or other materials are recovered from the solid waste stream for use in the form of raw materials in the manufacture of new products other than fuel for producing heat or power by combustion.

Recyclability – The ability of a product or material to be recovered from, or otherwise diverted from, the solid waste stream for the purpose of recycling.

Retainage – The amount withheld from the Contractor payment that is retained and subsequently released upon satisfactory completion of performance milestones by the Contractor.

Revision – A response to a BAFO request or a requested clarification of the Bidder’s Quote.

RMAN – Recovered Materials Advisory Notices provide purchasing guidance and recommendations for Recovered and Post-Consumer Material content levels for designated items.

Security Incident – means the potential access by non-authorized person(s) to Personal Data or Non-Public Data that the Provider believes could reasonably result in the use, disclosure, or access or theft of State’s unencrypted Personal Data or Non-Public Data within the possession or control of the Provider. A Security Incident may or may not turn into a Breach of Security.

Services – Includes, without limitation (i) Information Technology (IT) professional services, (ii) Software and Hardware-related services, including without limitation, installation, configuration, and training, and (iii) Software and Hardware maintenance and support and/or Software and Hardware technical support services.

Shall – Denotes that which is a mandatory requirement.

Should – Denotes that which is permissible or recommended, not mandatory.

Small Business – Pursuant to N.J.S.A. 52:32-19, N.J.A.C. 17:13-1.2, and N.J.A.C. 17:13-2.1, “small business” means a business that meets the requirements and definitions of “small business” and has applied for and been approved by the New Jersey Division of Revenue and Enterprise Services, Small Business Registration and M/WBE Certification Services Unit as (i) independently owned and operated, (ii) incorporated or registered in and has its principal place of business in the State of New Jersey; (iii)  has 100 or fewer full-time employees; and has gross revenues falling in one (1) of the six (6) following categories:

For goods and services - (A) 0 to $500,000 (Category I); (B) $500,001 to $5,000,000 (Category II); and (C) $5,000,001 to $12,000,000, or the applicable federal revenue standards established at 13 CFR 121.201, whichever is higher (Category III).

For construction services: (A) 0 to $3,000,000 (Category IV); (B) gross revenues that do not exceed 50 percent of the applicable annual revenue standards established at 13 CFR 121.201 (Category V); and (C) gross revenues that do not exceed the applicable annual revenue standards established at CFR 121.201, (Category VI).

Small Business Set-Aside Contract – means (1) a Contract for goods, equipment, construction or services which is designated as a Contract with respect to which bids are invited and accepted only from small businesses, or (2) a portion of a Contract when that portion has been so designated.”  N.J.S.A. 52:32-19.

Software – means, without limitation, computer programs, source codes, routines, or subroutines supplied by Provider, including operating software, programming aids, application programs, application programming interfaces and software products, and includes COTS, unless the context indicates otherwise.

Software as a Service or SaaS – means the capability provided to a purchaser to use the Provider’s applications running on a cloud infrastructure. The applications are accessible from various client devices through a thin client interface such as a Web browser (e.g., Web-based email) or a program interface. The purchaser does not manage or control the underlying cloud infrastructure, including network, servers, operating systems, storage or even individual application capabilities, with the possible exception of limited user-specific application configuration settings.

State – The State of New Jersey.

State Confidential Information – shall consist of State Data and State Intellectual Property  supplied by the State, any information or data gathered by the Contractor in fulfillment of the Contract and any analysis thereof (whether in fulfillment of the Contract or not).

State Contract Manager or SCM – The individual, responsible for the approval of all deliverables, i.e., tasks, sub-tasks or other work elements in the Scope of Work.  The SCM cannot direct or approve a Contract Amendment.

State Data – means all data and metadata created or in any way originating with the State, and all data that is the output of computer processing of or other electronic manipulation of any data that was created by or in any way originated with the State, whether such data or output is stored on the State’s hardware, the Provider’s hardware or exists in any system owned, maintained or otherwise controlled by the State or by the Provider.  State Data includes Personal Data and Non-Public Data.

State Intellectual Property – Any intellectual property that is owned by the State.  State Intellectual Property includes any derivative works and compilations of any State Intellectual Property.

State Price Sheet or State-Supplied Price Sheet – the bidding document created by the State and attached to this Bid Solicitation on which the Bidder submits its Quote pricing as is referenced and described in the Bid Solicitation.

Subtasks – Detailed activities that comprise the actual performance of a task.

Subcontractor – An entity having an arrangement with a Contractor, whereby the Contractor uses the products and/or services of that entity to fulfill some of its obligations under its State Contract, while retaining full responsibility for the performance of all  Contractor's obligations under the Contract, including payment to the Subcontractor.  The Subcontractor has no legal relationship with the State, only with the Contractor.

Task – A discrete unit of work to be performed.

Third Party Intellectual Property – Any intellectual property owned by parties other than the State or Contractor and contained in or necessary for the use of the Deliverables.  Third Party Intellectual Property includes COTS owned by Third Parties, and derivative works and compilations of any Third Party Intellectual Property.

Unit Cost or Unit Price – All-inclusive, firm fixed price charged by the Bidder for a single unit identified on a price line.

US CERT – United States Computer Emergency Readiness Team.

USEPA – United States Environmental Protection Agency.

Using Agency[ies] – A State department or agency, a quasi-State governmental entity, or an Intrastate Cooperative Purchasing participant, authorized to purchase products and/or services under a Contract procured by the Division.

Vendor – Either the Bidder or the Contractor.

Work Product – Every invention, modification, discovery, design, development, customization, configuration, improvement, process, Software program, work of authorship, documentation, formula, datum, technique, know how, secret, or intellectual property right whatsoever or any interest therein (whether patentable or not patentable or registerable under copyright or similar statutes or subject to analogous protection) that is specifically made, conceived, discovered, or reduced to practice by Contractor or Contractor’s Subcontractors or a third party engaged by Contractor or its Subcontractor pursuant to the Contract Notwithstanding anything to the contrary in the preceding sentence, Work Product does not include State Intellectual Property, Contractor Intellectual Property or Third Party Intellectual Property.

## CONTRACT-SPECIFIC DEFINITIONS

All-Inclusive Loaded Hourly Rate – The all-inclusive, loaded hourly rate shall include all direct and indirect costs including, but not limited to: overhead, fee or profit, clerical support, travel expense, training, safety equipment, materials, supplies, supervisory and managerial support and all documents, forms and reproductions thereof. Hourly rates also include portal-to-portal expenses which is the time spent traveling to and from the work site or employees’ normal workstations and shall be in included this rate. The hourly rate will begin when the technician arrives at the location and begins work. For purposes of this Bid Solicitation, any reference to hourly rates will mean All-Inclusive Loaded Hourly Rates.

ANSI – The American National Standards Institute.

Approved Equal – Supplies or services, or compatible items of construction whose quality, design, or performance characteristics are functionally equal or superior to an item specified.

ASME – The American Society of Mechanical Engineers.

Consultation – The recommendation for a course of action given by a Vendor {Contractor} once a site visit is completed.

DCA – The State of New Jersey, Department of Community Affairs. The Division of Codes and Standards establishes and enforces building codes, in partnership with the State’s municipalities, to protect the health and safety of New Jersey residents.

DLWD – The New Jersey Department of Labor & Workforce Development

Engagement – A site specific project performed by a Contractor.

Lockout/Tagout – Specific procedures and practices to safeguard employees from the unexpected energization or startup of machinery and equipment, or the release of hazardous energy during service of maintenance activities.

Monthly Preventative Maintenance Services: These are maintenance activities described in Bid Solicitation Section 4.6.1.1  performed once per month to intended to identify and prevent problems before they occur.

NJDOC – The New Jersey Department of Corrections.

NJDOT – The New Jersey Department of Transportation.

Overtime Hourly Rate – Work performed on Saturday or before or after regular work hours on Monday through Friday. Overtime Pay shall be in accordance with DLWD prevailing wage rate guidelines.

Project Manager – The Project Manager will have delegated authority sufficient to the State so as to be able to exercise day-to-day decision making on all operations and business matters, relating to performance of this Blanket P.O.

Regular Hourly Rate – Work performed between 8:00 AM to 4:30 PM, Monday through Friday.

State Building Manager (SBM) – The individual, as set forth by the Using Agency or Cooperative Purchasing Program participants, responsible for approval of all deliverables, i.e., tasks, sub-tasks or other work elements in the Scope of Work.

UCC – The Uniform Construction Code, Chapter 23 of Title 25 of the NJ Administrative Code

Vertical Transportation Equipment (VTE) – Elevators, escalators, lifts, dumbwaiters, hoists, moving walkways, or moveable bridges.

Worm Gear: A gear configuration in which a screw of worm meshes with the teeth of a gear.