SOF CONSTRUCT SIMULATOR FACILITY MC-130J

Pennsylvania Air National Guard

Harrisburg Air National Guard Base, Middletown, Pennsylvania

Project No. SHYQ149104

ADDENDUM #3

#### REVISIONS TO SPECIFICATIONS

  - Section 23 07 19 – HVAC Piping Insulation

    - Article 2.03.E.1 Application: DELETE “refrigerant gas” to read as follows:

- 1. Refrigerant suction and refrigerant liquid piping.

INSERT New Article 2.04 as follows:

- 2.04 HIGH TEMPERATURE FLEXIBLE ELASTOMERIC INSULATION

- A. Manufacturers:

- 1. Armacell

- 2. Aeroflex

- 3. K-flex.

- B. Insulation: Preformed flexible elastomeric cellular rubber insulation complying with ASTM C534/C534M Grade 1; use molded tubular material wherever possible.

- 1. Minimum Service Temperature: Minus 40 degrees F.

- 2. Maximum Service Temperature: 248 degrees F.

- 3. Connection: Waterproof vapor barrier adhesive.

- 4. Greenguard Gold certified. Conforms to UL 2818.

- 5. Tested, rated, and labeled to ASTM C518.

- 6. Flame Spread Index: Less than 25, conforms to ASTM E84.

- 7. Smoke Development Index: Less than 50, conforms to ASTM E84.

- C. Elastomeric Foam Adhesive: Air dried, contact adhesive, compatible with insulation.

- D. Protective coating for exterior applications: Acrylic paint from elastomeric insulation manufacturer.

- E. Application:

- 1. Variable Refrigerant Volume (VRF) hot gas discharge piping.

- 2. Optional for refrigerant suction and refrigerant liquid piping.

RENUMBER Articles 2.04 through 2.07 to read 2.05 through 2.08.

#### REVISIONS TO DRAWINGS

Drawing M603

Replace drawing M603 with attached drawing M603R3 in its entirety.