DATE:  June 24, 2026

PROJECT:  Fort Indiantown Gap - WWTP SBR 1 and Digester 1 Rehabilitation

SOLICITATION / BID NUMBER:  6100066141

OPENING DATE:  June 30, 2026

ADDENDUM NO. 4

GENERAL

A.	This Addendum constitutes part of the Project Manual and Contract. Should conflict occur between the Project Manual and items in this Addendum or between Drawings and this Addendum, the Addendum shall govern.

B.	Bidders are requested to attach a copy of this Addendum to the Project Manual in their possession.

C.	Work affected by items in this Addendum shall be appropriately adjusted to accommodate these changes.

D.	Sign and attach this addendum to your solicitation response.  Failure to do so may result in disqualification.

E.	The term “PROVIDE” as used in this Addendum and the Contract Documents means “FURNISH and INSTALL”.

BIDDERS QUESTIONS

1.	Question:  “Spec 012000 section 2 and the bid form state there are 750,000 gallons of sludge to be removed from digester #1 and #2.  Are we removing sludge from both digesters or only digester #1?  Do you have a quantity of removal per day throughout the project?  If we are to remove the sludge from digester #2, How much should we leave in the tank to be used for digester #1 seed sludge?”

Response:  Remove and dispose of all sludge (liquid, grit, solids, etc.) from Digester 1 in preparation for the work.  Remove and dispose of liquid sludge from Digester 2 to provide capacity for sludge wasting while Digester 1 is offline.  It is anticipated that both tanks will be emptied when work begins and Digester 2 will be emptied again before startup.  There is no defined daily quantity (gallons/day) - remove sludge as needed to meet project requirements and in accordance with the Contract Documents.  Seed sludge is not required for startup of Digester 1.

2.	Question:  “Spec 012000 section 3 requires to use dewatering boxes to dewater the grit. This also says we need to haul and dispose off site the grit as well as the water we remove. If this is for quantifying the amount of disposal. Is it possible to quantify the amount left in the tanks once the owner stops pumping by measuring cubic feet and converting to gallons. Disposal would be based on the gallons in the tank prior to removal. For the bid form value, the total could be figured at the full depth of 18” and adjusted to final depth.”

Response:  Measurement and payment for SBR and Digester Grit Removal and Disposal shall be in accordance with the Contract Documents.  Solids (sediment, grit, rags, debris, sludge, etc.) remaining in the Digester and SBR SHALL NOT be disposed of at a municipal wastewater treatment facility.

3.	Question:  “Are Milliken valves specified qualify as an exception to the BABA requirements?”

Response:  The successful bidder shall comply with the Build America, Buy America Act in accordance with Article 20.20 of the General Conditions to the Construction Contract DMVA v6.

4.	Question:  “Existing DP and ORP probes are tied to the SBR control system.  If they are to be replaced would you prefer that Aqua provide them?”

Response:  Install DO and ORP probes/sensors in accordance with Specification Section 46 53 53 2.2.E.9.