Date:	    July 9, 2026

To:        All Bidders for RFQ FMD BAS Upgrade

From:  	Department of General Services

Office of Business and Acquisition Services (OBAS)

Subject:  Addendum #1 – RFQ FMD BAS Upgrade

This addendum is to make additions, changes, and clarifications to the solicitation referenced above.

Change #1 – Exhibit A, Section 6.A.4. Additional language has been added.

- This project shall be considered complete when:

- Graphics accurately represent field operation.

- All identified points communicate properly.

- Operator-adjustable setpoints can be modified from the building automation system (BAS).

- Dampers and valves respond to BAS commands and display correct feedback.

- Chiller, pump, and cooling tower statuses display correctly.

- Economizer sequences operate as intended.

- Invalid values (NaN) have been eliminated.

- Functional testing has been completed and observed by the FMD Contract Administrator or FMD Designated Representative.

- Contractor shall email the exception report to the FMD Contract Administrator or FMD Designated Representative within 15 calendar days of completion of services.

Change 2 – RFQ Key Action Dates has been changed as follows:

## Key Action Dates

Listed below are the important action dates and times by which actions must be taken or completed.  If OBAS finds it necessary to change any of these dates, it will be accomplished by addendum to this RFQ.  ALL DATES AFTER THE DEADLINE FOR FINAL BID SUBMISSION ARE APPROXIMATE AND MAY BE ADJUSTED AS CONDITIONS INDICATE, WITHOUT ADDENDUM TO THIS RFQ.