## Requirements
Basic PM to Include:
Category | Inspection Item | Notes
Lubrication | Check engine oil level and top off as required.
Lubrication | Inspect engine for oil leaks at seals, gaskets, and drain plugs.
Fuel System | Check fuel supply level and condition; verify tank integrity and vent condition. | Diesel Only
Fuel System | Inspect fuel lines, pumps, and connections for leaks or sweating. | Diesel Only
Fuel System | Drain water and sediment from fuel water separators/primary filters. | Diesel Only
Fuel System | Verify gas supply pressure at inlet and confirm pressure is within manufacturer's specified range. | Natural Gas Only
Fuel System | Inspect gas lines, fittings, and flexible connectors for leaks | Natural Gas Only
Fuel System | Inspect gas regulator and shutoff valve for proper operation and signs of damage or corrosion. | Natural Gas Only
Cooling System | Check coolant level and radiator cap integrity.
Cooling System | Check and record freeze protection (glycol concentration); adjust as required.
Cooling System | Inspect fan drive belts for condition and proper tension; adjust as required.
Cooling System | Inspect coolant hoses, pipes, and radiator core for leaks or damage.
Cooling System | Inspect water pump for shaft play, mounting security, and weep hole leakage.
Cooling System | Check operation of jacket water heater and control thermostats.
Cooling System | Verify thermostat operation and coolant flow during engine exercise.
Cooling System | Inspect radiator for debris/obstruction and check fan shroud for integrity.
Batteries | Clean and protect battery terminals; inspect cables for security.
Batteries | Check and record starting battery float voltage and specific gravity.
Batteries | Check electrolyte levels and add distilled water as required.
Batteries | Perform a battery load test and record voltage drop on start.
Electrical | Check battery charger for proper operation and record voltages.
Electrical | Inspect starter motor, cables, and solenoid for condition and security.
Electrical | Visually inspect exciter assembly, stator, and field windings for cleanliness.
Exhaust | Inspect manifold, exhaust pipes, flexes, and turbochargers for leaks or soot.
Mechanical | Inspect louvers, vents, and louver actuators for obstruction and proper operation.
Mechanical | Inspect enclosure seals, weatherstripping, and housing for integrity and weather-tightness.
Mechanical | Inspect fan guard and air inlet screens for cleanliness and security.
Mechanical | Check governor linkage and fuel rack/air-fuel mixer for proper operation.
Controls | Verify operation of auto-start sequence.
Controls | Verify operation and accuracy of AC and engine instruments/meters.
Operation | Perform a 15-minute no-load exercise run.
Operation | Monitor and record system frequency and voltage; adjust if necessary.
ATS | Visually inspect ATS components, connections, and cabinets.
ATS | Check indicator lamps and verify all insulating parts are free of cracks.
ATS | Inspect all main current arcing contacts for pitting or heat discoloration.
ATS | Calibrate and adjust all time delay devices and power sensing controls.
Major PM Includes:
Category | Service Item | Notes
Foundation | Include all items from the Basic PM Scope.
Lubrication | Drain engine oil and refill with fresh, manufacturer-approved oil.
Lubrication | Replace all engine oil filters and document date of replacement.
Fuel System | Replace primary and secondary fuel filters (if applicable). | Diesel Only
Fuel System | Clean fuel sediment bowls and inspect fuel tank vents for obstructions. | Diesel Only
Fuel System | Remove and inspect spark plugs, clean and regap | Natural Gas Only
Air System | Replace engine air filter(s) and inspect induction piping for integrity.
Air System | Clean and service crankcase breathers as required.
Cooling System | Flush cooling system and replace with fresh coolant.
Cooling System | Replace coolant filter(s) and service radiator fins as necessary.
Cooling System | Perform coolant litmus test and document results.
Electrical | Inspect and tighten all high-voltage power cable terminations.
ATS | Perform a simulated utility power failure to initiate a connected load transfer test; observe and record all pertinent voltage, current, and time data on both generator and ATS. | Coordinate notifications and schedule with City Engineering before load transfer.
Oil Analysis Includes:
Category | Service Item | Notes
Engine Oil | Test for wear metals, total base number, and viscosity.
Engine Oil | Test for fuel dilution | Diesel Only
Load Test Includes:
Category | Service Item
Load Bank | Connect resistive load bank and perform a 2-Hour Load Test.
Load Bank | Apply load in 25% increments; run for 15 minutes at each step.
Load Bank | Run unit at 100% nameplate capacity for a minimum of 1 hour.
Load Bank | Record and report engine hours, oil pressure, coolant temp, voltage, and frequency at 15-minute intervals.

## Anticipated Schedule
| Basic PM | Oil Analysis | Load Testing & Major PM | Notes:
Frequency: | 2x Yearly | 1x Yearly | 1x Yearly
2026 | B, C (once) | A, B, C | A | Exclude Bartillon and Truax Generator from 2026 Service. Do basic PM once in 2026.
2027 | A, B, C | A, B, C | B
2028 | A, B, C | A, B, C | C
2029 | A, B, C | A, B, C | A
2030 | A, B, C | A, B, C | B
Note: On Load Testing/Major PM years, that service will replace one scheduled Basic PM service.

## Generator Details
"Group" | Major PM When? | Agency | Property | Address | In Service | Fuel_Type |  |  |  | Voltage_and_Phase | Watts | Indoor/Outdoor
A | 2026, 2029 | Sewer Utility | Lift Station - Carroll | 622 N Carroll St., Madison, WI 53703 | 2019 | Natural Gas | Kohler | KG45 | 33MFGMGC0004 | 208 V 3 ph | 45 kW | Outdoor
A | 2026, 2029 | Sewer Utility | Lift Station - Fremont | 2405 Fremont Ave., Madison, WI 53704 | 2019 | Natural Gas | Cummins | 125GGHJ | K170270882 | 208 V 3 ph | 40 kW | Outdoor
A | 2026, 2029 | Sewer Utility | Lift Station - James | 3135 James St., Madison, WI 53714 | 2019 | Natural Gas | Cummins | C45 N6 | H190623179 | 208 V 3 ph | 45 kW | Outdoor
A | 2026, 2029 | Sewer Utility | Lift Station - Cherokee #1 | 5121 Comanche Way, Madison, WI 53704 | 2019 | Natural Gas | Kohler | KG40 | 33MDGMGJ0051 | 208 V 3 ph | 40 kW | Outdoor
A | 2026, 2029 | Sewer Utility | Lift Station - Woodley | 2712 Waunona Way, Madison, WI 53704 | 2019 | Natural Gas | Generac | QT02524GNSNA | 3001575231 | 208 V 3 ph | 45 kW | Outdoor
A | 2026, 2029 | Engineering | Engineering Ops - Garage | 1600 Emil St.,Madison WI53713 | 2017 | Natural Gas | Olympian | G300LG6 | GXJ04496 | 480 V 3 Phase | 300 kW | Outdoor
A | 2026, 2029 | Streets | Streets West | 1501 W Badger Rd, Madison, WI 53713 | 1981 | Diesel | Onan | 155.00FE-15R/23785L | G810583202 | 208 V 3 ph | 155 kW | Outdoor
B | 2027, 2030 | MWU | IT Network Operations Center | 119 E Olin Ave., Madison, WI 53713 | 2003 | Diesel | Cummins | DGDB-5689823 | H040682650 | 208 V 3 ph | 100 kW | Outdoor
B | 2027, 2030 | Sewer Utility | Lift Station - Debs Rd | 407 Debs Rd., Madison, WI 53704 | 2020 | Natural Gas | Kohler | 20RESCL | 339VGVFP0237 | 240 V 1 ph | 20 kW | Outdoor
B | 2027, 2030 | Sewer Utility | Lift Station - Arbor Hills | 2714 W. Beltline Highway | 2021 | Natural Gas | Generac | SG00080GG169.0N18HPSYA | 3008283178 | 208 V 3 ph | 80 kW | Outdoor
B | 2027, 2030 | Sewer Utility | Lift Station - Harper | 3402 Harper Rd. Madison, WI 53704 | 2023 | Natural Gas | Generac | SG0050GG264.5S18TPYYA | 3011952391 | 208 V 3 ph | 50 kW | Outdoor
B | 2027, 2030 | Parking | Garage - South Livingston | 111 S Livingston St. Madison, WI 53703 | 2018 | Natural Gas | Cummins | C60 N6 | E180360406 | 208 V 3 ph | 60 kW | Indoor
B | 2027, 2030 | Parking | Garage - State St Capitol | 214 N Carrol St., Madison, WI 53703 | 2019 | Natural Gas | Cummins | C60 N6H | G170217933 | 208 V 3 ph | 60 kW | Indoor
B | 2027, 2030 | Parking | Garage - State St Campus/Frances | 430 N Frances St, Madison, WI 53703 | 2019 | Natural Gas | Cummins | C30 N6H | K180446598 | 208 V 3 ph | 30 kW | Indoor
C | 2028, 2031 | Sewer Utility | Lift Station - Thurber | 3325 Thurber Ave., Madison, WI 53714 | 2024 | Natural Gas | Cummins | C20N6 | A230197917 | 208 V 3 ph | 20 kW | Outdoor
C | 2028, 2031 | Sewer Utility | Lift Station - Veith | 4100 Veith Ave., Madison, WI 53704 | 2024 | Natural Gas | Generac | SC0080GGZ269.0N18HPSYA | 3013404212 | 208 V 3 ph | 80 kW | Outdoor
C | 2028, 2031 | CDD | Bartillon Men's Shelter | 1902 Bartillon Dr., Madison, WI 53704 | 2026 | Natural Gas | Gillette | SP-6500-3-4N2 | TBD | 480 V 3 ph | 650kW | Outdoor
C | 2028, 2031 | Fleet | Fleet Services - Nakoosa | 4151 Nakoosa Trail, Madison, WI 53714 | 2024 | Diesel | Cummins | C150D2RE | G220119573 | 480 V 3 ph | 150 kW | Outdoor
C | 2028, 2031 | Police | Police - Midtown District | 4020 Mineral Point Rd, Madison,WI 53705 | 2018 | Natural Gas | MTU Onsite | 12V0183GS400 | NA | 480 V 3 ph | 400 kW | Outdoor
C | 2028, 2031 | Police | Police - East District | 809 Thompson Dr., Madison, WI 53714 | 2023 | Natural Gas | Generac | SG0150GG269.0S18HPLYE | 3012053034 | 208 V 3 ph | 150 kW | Outdoor
C | 2028, 2031 | Sewer Utility | Lift Station - Truax | 2701 Anderson St, Madison, WI 53704 | 2026 | Natural Gas | Generac | SG060 |  | 208 V 3 ph | 60 kW | Outdoor
C | 2028, 2031 | Streets | Streets East | 4602 Sycamore Ave,Madison,WI 53704 | 2024 | Natural Gas | Generac | SG100 | 3013455813 | 208 V 3 ph | 100 kW | Indoor
HOLD FOR NOW |  | Fire | Fire Station 01 | 316 W Dayton St., Madison, WI 53703 | 2015 | Diesel | Cummins | DFEK-1514856 | G150849507 | 208 V 3 ph | 500 kW | Indoor - Basement
|  |  |  | Capacity Tier | kW Range |  | A | B | C
|  |  |  | Tier 1 (Small) | 0 – 100 kW |  | 5 | 7 | 4 | 16
|  |  |  | Tier 2 (Mid) | 101 – 250 kW |  | 1 | 0 | 2 | 3
|  |  |  | Tier 3 (Large) | 251 – 500 kW |  | 1 | 0 | 1 | 2
|  |  |  | Tier 4 (Heavy) | 501+ kW |  | 0 | 0 | 1 | 1