Date:	August 27, 2026

To:   All Bidders for IFB – Emergency Generator; Building #063, CR-25-294216

From:  Department of General Services

Office of Business and Acquisition Services (OBAS)

Subject:  Addendum #4 - IFB – Emergency Generator; Building #063, CR-25-294216

This addendum is to make additions, changes, and clarifications to the solicitation referenced above.

Change 1 – Per Addendum 4, IFB Instructions, B. Minimum Requirements, 2. Insurance, has been revised to clarify as follows:

- Insurance:

A Bidder must submit current proof of insurance for the following:

  - General Liability

  - Commercial Automobile Insurance

  - Worker’s Compensation

A certificate of insurance (COI) may be provided as proof of insurance.  The COI or proof of insurance documents will be named Attachment 78, Proof of Insurance, and be submitted with the bid.  Endorsements to insurance policies are not required for bid submission.  Endorsements to insurance policies are only required by the winning Bidder as indicated in Attachment 910, Sample Agreement.

Change 2 – Per Addendum 4, IFB Instructions, B. Minimum Requirements, 3. has been revised to clarify as follows:

- References: Bidders must provide three (3) or more references.  Required Attachment 5, Bidder References, must be completed and submitted with the bid submission.  NOTE: References to include satisfactory job performance on operations within the last five (5) years that are similar to parking lot management services  Emergency Generator Maintenance Services as required in this solicitation.

Change 3 – Per Addendum 4, IFB Instructions, Attachment 7, Proof of Insurance, has been revised to clarify as follows:

A Bidder must submit current proof of insurance as Attachment 78 for the following:

- General Liability

- Commercial Automobile Insurance

- Worker’s Compensation

Change 4 – Per Addendum 4, IFB Instructions, Attachment 9, Sample Agreement, Exhibit A, Scope of Work, 5. Service Details, D. Parking has been revised to clarify as follows:

“The State does not provide parking, however, off-loading of equipment and materials may be performed at the building’s loading dock if permission is obtained in advance from the FMD Contract Administrator or FMD Designated Representative and sufficient space is available. Contractor will park on city streets along P street, between 7th Street and 8th Street, utilizing any of the six (6) spaces on the western side of the block (7th Street side).”

Change 5 – Per Addendum 4, IFB Instructions, Attachment 9, Sample Agreement, Exhibit A, Scope of Work, Section 6. Work Details, A. Semi-Annual-Preventive Maintenance, Item15. has been revised for clarification as follows:

- The Contractor shall provide a temporary standby generator whenever the facility’s permanent standby generator is out of service for scheduled maintenance or repairs. The temporary generator shall be sized to support all critical loads, including fire pumps, as required by NFPA 20 (2019 Edition), Sections 9.2, 9.3, and 9.6.u. Annual Preventive Maintenance and Two–Hour Load Bank Testing can be done at the same time and will require the generator to be out of service. Semi-annual Preventive Maintenance must be done by itself and may not take the generator out of service unless repairs are necessary.

Change 6 – Per Addendum 4, IFB Instructions, Attachment 9 Sample Agreement, Exhibit A, Scope of Work, 6. Work Details, A, Semi-Annual-Preventive Maintenance, item 17. has been revised for clarification to read as follows:

17.	Connection Requirements - Temporary generator shall be connected to the existing building Automatic Transfer Switch (ATS) and emergency power system, at the main switching board in SWBD-MSBG. Connection shall comply with NFPA 20 Sections 9.2, 9.3, 9.6, NFPA 110 for emergency power system performance and testing, and local electrical codes and safety standards. There is no existing docking or tap provision.

Change 7 – Per Addendum 4, IFB Instructions, Attachment 9, Sample Agreement, Exhibit A, Scope of Work, 6. Work Details, C. Two-Hour Load Bank Testing, Item 4. has been added to clarify as follows:

4. The tie-in location for the Two-Hour Load Bank Testing is at the Generator Control Panel located on P Steet, between 7th Street and 8th Street, on the western side of the block (7th Street side).

Change 8 – Per Addendum 4, IFB Instructions, Attachment 9, Sample Agreement, Exhibit A, Attachment 1, Equipment List, has been revised to clarify there are five (5) transfer switches as follows:

Service shall be applicable for the following equipment:

| QTY | EQUIPMENT DESCRIPTION | MANUFACTURER | MODEL # | SERIAL # |
| --- | --- | --- | --- | --- |
| 1 | ENG. Family HCPXL78.INZS | Caterpillar | 3512C | N/A |
| 1 | BATTERY Charger | Sens | NRG24- 20HCLS | 487117-47-19 |
| 2 | Battery | CAT | 153-5720 | 210 ah CAP @ 20 HRS, 465 RC 12 v |
| 1 | Generator | Caterpillar | LYH00422 | S/N GAF00506 |
| 1 | Power Transfer Switch ATS-R1 | ASCO 7000 Series Power Transfer Switch ATS-R1 | G7ADTBB 32000N5X C | S/N # 1981832 WE |
| 1 | ATS Automatic Transfer switch | ASCO 7000 Series Power Transfer Switch ATS-E1 | J07ATBB3 0400N5XC | S/N 1981833 RE |
| 1 | ATS Automatic Transfer switch | ASCO 7000 Series Power Transfer Switch ATS-S1 | G7ADTBB 31200N5X C | S/N 1811794 WE |
| 1 | Electrical Fire Pump Controller with Automatic Transfer Switch ATS-FP1 | Hubbell Metron | MPT700-200-480C MTS-400Z | S/N 24360967 |
| 1 | Electrical Fire Pump Controller with Automatic Transfer Switch ATS-FP2 | Hubbell Metron | MPT700-200-480C MTS-400Z | S/N 24373436 |